## Discussion Points
GC0079 - Frequency Changes During System Disturbances - Workgroup Issue Tracker
Code Governance: Ellen Bishop
Action/Risk Management:
Line No. | Meeting Date | Meeting No. | Agenda Item | Topic | Workgroup Discussion Point | Category | Raised by | Status | Owner | Target Completion Date | Updates
1 | 2016-05-17 | 41 | Ecofys Update | Solar PV generation volumes | Solar proliferation has continued as projected in Ecofys' 2014/15 analysis. At least 50% of sub-5MW distribution-connected generation is thought to be Solar PV and this growth is expected to continue. | Point to note | MD | Resolved
2 | 2016-05-17 | 41 | Ecofys Update | Solar PV generation volumes | Whilst concern was expressed at the impact rapid PV growth had on the generators in scope for a GC0079 protection settings change, GS's previous analysis had shown that PV sensitivity to the CBA numbers made little difference | Point to note | Workgroup | Resolved
3 | 2016-05-17 | 41 | Ecofys Update | Solar PV generation volumes | MK did not consider that Adam Dysko's previous study work needed to be updated to reflect the revised Solar PV figures, but again, it was an important point to note that increased distributed generation increased the islanding risk in general | Point to note | JR | Resolved
4 | 2016-05-17 | 41 | Ecofys Update | Solar PV generation volumes | The Ecofys study work needs to be supplemented with a distribution of individual site volume, and a monthly trend on growth rather than just yearly. This will then be finalised with their previous study work and published. | Action | GS | Resolved | MD/GS | 2016-06-27 | GS to circulate Ecofys study for comment (sent post meeting 29/6/16)
5 | 2016-05-17 | 41 | Ecofys Update | DG generation volumes | A previous action remains with the DNO reps to provide GS their sub-5MW generation figures (removing domestic schemes). GS has circulated an email explaining what he needs. DNO reps should submit their information as soon as possible | Action | Workgroup | Resolved | DNO Reps/GS | 2016-07-08 | Some outstanding data from DNOs
6 | 2016-05-17 | 41 | TCMF Update | Commercial Considerations | The Transmission Charging Methodology Forum (TCMF) provided feedback to GS during a presentation on potential funding options (including BSUoS). - Not convinced on justification for funding through BSUoS - particularly as some parties incurring the short-term cost may not be around to realise the long-term benefit - Seek further guidance from Ofgem, particularly as this is a networks issue not just a commercial one - Concern over the management cost - this could be a blank cheque (GS estimated £10m for the work, £33m/year recurring benefit of complete GC0035 + GC0079 changes) - GC0079 cannot change charging regimes (though an SO charging review is in progress) | Point to note | GS | Resolved | GRS | 2016-12-31 | Comprehensive list of options produced for 11/10/16 meeting. Awaiting completion of actions.
7 | 2016-05-17 | 41 | TCMF Update | Phase 1 compliance | The success rate of achieving compliance needs to be factored into the GC0079 recommendation. This is still a moving target for GC0035, which is due to give an update at the DCRP on 02/06/16 | Point to note | CMD | Point of note
8 | 2016-05-17 | 41 | TCMF Update | Commercial Considerations | Need to ensure that benefits and costs from Phase 1/2(/3) are properly set out in the workgroup report and not double-counted. GS confirmed these would be disaggregated in the workgroup report | Point to note | JD | Would it be possible from your immediate contacts, ie probably relevant experts in your own companies to provide information about VS protection along the following lines? One set of data for each manufacturers’ relay type:
9 | 2016-05-17 | 41 | TCMF Update | Commercial Considerations | Workgroup members are requested to consider their preference on the funding options set out, consider potential other options, and the DNO reps requested to consider managing the work within their own organisations | Point to note | Workgroup | Resolved
10 | 2016-05-17 | 41 | TCMF Update | Commercial Considerations | MK and GS to resume discussions with Ofgem on the funding route and what should be included in the WG report. | Action | Workgroup | resolved | GS/MK |  | Replaced by line 35
11 | 2016-05-17 | 41 | Workgroup Report | Costs | The table of costs on page 14 needs to be updated to include site visit admin and test witnessing costs | Action | IK | Resolved | GS | 2016-06-27 | Revisit following drafting
12 | 2016-05-17 | 41 | Workgroup Report | Vector Shift | Workgroup consideration of Vector Shift needs to be added. Section 5.24 in particular needs to be adjusted to reflect workgroup thinking on this topic. It was also noted that VS is not allowed in Ireland for synchronous machines as it cannot detect islanding (need to confirm this in writing) Vector Shift is part of the consideration for GC0079 Phase 3 | Point to note | ML | Point of note | GS/MK/ML | 2016-07-26 | Call with ESB arranged for 1/7/16
13 | 2016-05-17 | 41 | Workgroup Report | Voltage Control v Power Factor mode | Scottish DNOs get generation to operate in Voltage Control mode - this will impact the GC0079 recommendation and needs to be checked against a previous discussion between MK with GM and AMPS (details were circulated at the time). Also note there is a meeting on 28/06 at ENA with ML/MK on use of Voltage Control for DG. For more info, contact MK, ML or RJW | Action | JD | Point of note | MK | 2016-06-27
14 | 2016-05-17 | 41 | Workgroup Report | LoMP | DNOs were requested to provide their own view of the ratio of Loss of Mains Protection being RoCoF or not (excluding domestic). The current workgroup report assumption is 50/50. | Action | ST | Resolved | DNO Reps | 2016-07-08
15 | 2016-05-17 | 41 | Workgroup Report | Site visits | The workgroup report needs to clarify whether generator owners can facilitate their own settings change, and how/if this is funded | Point to note | Workgroup | Resolved | MK/GRS | 2016-08-30
16 | 2016-05-17 | 41 | Workgroup Report | Exemptions | Phase 1 provided for generation exemptions for compliance - would the same wording be used in the workgroup report for Phase 2? Would such a process be needed? | Action | GM | Point of note | MK/GS | 2016-06-27 | Agreed to draft 1.0Hz/s for all
17 | 2016-05-17 | 41 | AOB | Meeting Dates | RJW to provide the meeting dates and venues for the remainder of 2016 | Action | Workgroup | Resolved | RJW | ASAP
18 | 2015-10-22 | 35 |  | Enhanced Frequency Response | NGET to provide more details on the Enhanced Frequency Response tender exercise currently on-going by NGET, particularly re. obtaining response from batteries and storage devices | Action | JD/GE | Resolved | GS/RJW | When tender results published | http://www2.nationalgrid.com/Enhanced-Frequency-Response.aspx
19 | 2015-11-23 | 36 |  | Over-frequency | Recommend resetting of protection on sub 5MW generators as part of the intended recommendations (from previous G59/1 change of over-frequency to 51.5hz) - placeholder action to note for WG report | Point to note | ML | Resolved | MK/GS | TBC | text incorporated into draft WG report
20 | 2016-02-24 | 39 |  | Risk Assessment | JA to update his risk assessment paper and to recirculate for workgroup comment | Action | JA | Resolved | JA | Aug
21 | 2016-03-23 | 40 |  | Workgroup Terms of Reference | Circulate agreed Terms of Reference following Grid Code and Distribution Code Review Panel approvals New action pending | Action | Workgroup | Resolved | RJW | ASAP | DCRP rejected ToRs pending resolution of Phase 1 issues
22 | 2016-04-20 | 40A |  | Dead Times | Write up general proposition re longer dead times for individual risk mitigation | Action | MK | Resolved | AD | ASAP
23 | 2016-04-20 | 40A |  |  | Confirm tripping time wording OK | Action | MK | Resolved
24 | 2016-04-20 | 40A |  | RoCoF Protection | Re. RoCoF protection requirements - stability type testing machines <50kW was a defacto ride through requirement. SB to seek out where misinformation was arising, and to use the offices of the DNOs to try to resolve. Discuss RoCoF ridethrough and escalate to GS/MK if required. | Action | SB/CMD | Resolved
25 | 2016-06-29 | 42 | Workgroup Report | Probability and Risk Assessment | Further evidence and references need to be added in this section | Point to note | JD |  | GD/MK
26 | 2016-06-29 | 42 | Workgroup Report | Battery Storage | Report needs to comment on battery storage. GS to clarify postion on intertrips - whether intertrips should not be used for load management schemes but are acceptable for Loss of Mains protection. | Point to note | GS | Active | GS | 2016-07-25 | related to EFR
27 | 2016-06-29 | 42 | Workgroup Report | Island Formation | Section 5.7 needs to clarify that islanding information is based on engineering judgement. | Action | MK/GS | Resolved | MK |  | Included in redraft
28 | 2016-06-29 | 42 | Workgroup Report | Change in demand or network configuration | DNOs to consider how to deal with the situation where risk assessment may no longer be valid due to changes in demand or network configuration. | Action | DNO members | Active | MK | 2017-04-30 | MK to discuss separately with DNOs. Remain an open action 12/12/ Mk to follow up Raise with ENFG? MK to confirm
29 | 2016-06-29 | 42 | Workgroup Report | 5.21 Mitigations | Clarify difference between preventing islanding and mitigation following islanding. | Action | IK | Resolved | GS/MK | 2016-07-25 | Included in redraft
30 | 2016-06-29 | 42 | Workgroup Report | Cost Benefit Analysis | All to review and and provide any comments on this section. (from 5.27) | Action | MK | Resolved | All | 2016-07-25
31 | 2016-06-29 | 42 | Workgroup Report | Cost Benefit Analysis | All to revise figures in Tables 2 and 3 noting most realistic and worst case scenario. These will be circulated to all. Instead of a full workgroup meeting in July, a small subgroup of volunteers will go through and agree figures to be used in the report. | Action | All | Resolved | MK | 2016-07-25
32 | 2016-06-29 | 42 | Workgroup Report | Comments | All to provide any further comments on the remainder of the report. | Action | All | Resolved | All | 2016-07-08
33 | 2016-06-29 | 42 | Workgroup Report | Secured Event | In section 5.78, refer to SQSS for clear definition of 'secured event' | Point to note | MK | On Hold | GS/MK | 2016-07-25
34 | 2016-06-29 | 42 | Next Steps | Commercial | Some expertise is needed to consider how the work will be funded (BSUoS, DUoS?). MK to circulate his note specifying what is required from DNO commercial expertise on the workgroup. This has already been raised at COG. DNO members also to raise this within their own organisations. | Action | MK | Resolved | MK/DNOs | 2016-07-25 | email sent to DNOs on 30/6
35 | 2016-06-29 | 42 | Next Steps | Funding | Seek further Ofgem advice on funding. | Action | MK | Resolved | GS/MK | Aug
36 | 2016-06-29 | 42 | Next Steps | Benefit | Benefit calculations can be refreshed in next several weeks with 2016 FES data. | Action | GS | Resolved | GS | 2016-08-31
37 | 2016-06-29 | 42 | AOB | Vector Shift | An event occurred on 22 May where a NG 400kV circuit tripped (and successfully reclosed) in the South West causing an estimated 400MW of local generation to disconnect. Analysis has shown that at least some of the generation tripped on vector shift. The Strathclyde University Study had shown generators using vector shift for loss of mains were more likely to trip than those using RoCoF. JP to share the outcome of studies on a similar Irish incident with the group when complete. GS to follow up NG investigations on 22 May incident and link with GC0079 ToR. | Action | AH | Resolved | JP/GS | 2016-07-25 | GS to discuss with AH
38 | 2016-06-29 | 42 | Next Meeting | July | First part of meeting will be a subgroup reviewing costs (see Line 31). 2-3pm Remaining workgroup members will dial in. RJW to confirm arrangements. | Action | MK | Resolved | RJW | 2016-07-15
|  | 43 | Next Meeting | July | Publish Ecofys report on GC0079 page | Action | GS/RJW | Resolved
36 |  | 44 | Next Meeting |  | Clarify ToR following DCRP rejection | Action | MK | Resolved
|  | 45 | Next Meeting |  | Circulate Excel backing sheet for provided costs/benefits, explaining assumptions – seek workgroup comments – | Action | · MK/GS/RJW/All | Resolved
|  | 46 | Next Meeting |  | Tidy up workgroup issue tracker, clarifying WG report points to note and resolved actions | Action | RJW | Resolved
|  | 47 | Next Meeting |  | Work through on-going actions for WG report (see line above), particularly around DG data volumes in FES 2016 and Wk 24 | Action | · MK/GS/All | Resolved
|  | 48 | AOB |  | Send dates again for remainder of the year | Action | RJW | Resolved
37 | 2016-09-27 | 49 | Cost Benefit Analysis | Report | Clarify and simplify the narrative around the sceanarios notably the analysis | Point to note | GS | Resolved | GS
38 | 2016-09-27 | 49 | Cost Benefit Analysis | Cost Benefit Analysis | Can we take out turn figures from the 2015/2016 to see actual fgures in the analysis | Point to note | GS | Resolved | GS
39 | 2016-09-27 | 49 | Cost Benefit Analysis | Cost Benefit Analysis | Clarity over the role of Pumped Storage in the analysis data | Point to note | GS | Resolved | GS | 2016-11-30 | PS not explicitly modelled: to be included in next update
40 | 2016-09-27 | 49 | Cost Benefit Analysis | Cost Benefit Analysis | NPV should be carried out for future years | Point to note | MK | Resolved
41 | 2016-09-27 | 49 | Cost Benefit Analysis | Cost Benefit Analysis | Reflect on how figures notably £20 could be different and produce a table with £10 and build in clarity of narrative | Point to note | IK | Active | GS
42 | 2016-09-27 | 49 | Cost Benefit Analysis | Cost Benefit Analysis | Consider break down the figures from pg 10 further | Point to note | ML | Active | GS
43 | 2016-09-27 | 49 | Vector Shift | Vector Shift | Refine a specification for further work - whether this is part of this w/g's aim or not? (To include: Research Northern Ireland's data and analysis work and views as to next steps for this workgroup enable collaboration - what to include and how best to discharge analysis on VS) | Action | MK | Resolved | GS
44 | 2016-09-27 | 49 | Vector Shift | Vector Shift | Understand ENFG position - Get a detailed view of what actions should be taken from the ENFG response | Action | ML | Resolved | MK |  | Advised to carry on research; to be presented back to ENFG in due course
45 | 2016-09-27 | 49 |  | Vector Shift | Obtain more data when events occur set up a system of collecting relevant data post transmission faults | Point to note | ML | Active | GS |  | Mechanism is already in place. Discussoin required over quality of response. GS not really a w/g action - it feels that this is something between NG and DNO's. Leave open to review at next meeting. MK suggesting we move to a different forum. Liaison between transmission and distribution we need to make sure this doesn't fall between the cracks MQ. Methods not ideal but not in a position to make changes
56 | 2016-09-27 | 49 | Cost Benefit Analysis for Vector Shift | Vector Shift | Reassess the cost part of the CBA with Vector Shift reset/replacement in mind | Action | MK | Resolved | MK |  | Circulated to WG
47 | 2016-09-27 | 49 | Next meeting |  | Confirm remaining dates for this year as 15/11 and 13/12 | Action | EB | Resolved | EB
48 | 2016-11-15 | 50 | Commercial considerations | Workgroup report | Reissue the workgroup report to the group | Action | MK | Resolved | EB
49 | 2016-11-15 | 50 | Commercial considerations | Commercial considerations | Funding options need to be articulated, probably in matrix form. Waiting progress from Electricity North West colleagues. MK to chase | Action |  | Resolved | MK | 2016-12-12
50 | 2016-11-15 | 50 | Vector Shift | Vector Shift | Agreed that UoS should be asked to investigate relative risk of VS versus RoCoF on the same basis as the absolute RoCoF risk was established for Phase 1. If VS has more likelihood of islanding, consider banning future use. GRS to create short form specification for UoS to make a proposition. | Action | GS | Resolved | GS/MK | 2016-11-18
51 | 2016-11-15 | 50 | Action Plan |  | Update overall plan and create Gantt chart | Action | GS | Resolved | GS | 2016-11-18
52 | 2016-11-15 | 50 | Tracker | Revised ToRs | All to comment on revised ToRs | Action | MK | Resolved | ALL | 2016-11-18
53 | 2016-11-15 | 50 | Action Plan | Inverter testing | All to coment on UoS proposal | Action | MK | Resolved | ALL | 2016-11-25
54 | 2016-11-15 | 50 | Action Plan | Future meeting dates | Cancel 13/12. Telecon on 12/12 1330-1530. Face to face meeting Tuesday 24/1 | Action | MK | Resolved | EB | 2016-11-25
55 | 2016-12-12 | 51 | Vector Shift |  | Peter to send out Vector Shift assessment plan and information approach. National Grid to send information out asap and DNO's to respond and feedback | Action | GS | Resolved | GS | 2016-12-30
56 | 2016-12-12 | 51 | Workgroup Plan | Workgroup Plan | Workgroup members are aware of and engaged with the plan put forward by GS | Point to note | GS | Active | GS/All | Ongoing
57 | 2016-12-12 | 51 | Vector Shift | Vector Shift Research and Procurement | Circulate research and methodology by Adam Dysko - workgroup to respond ahead of Christmas break | Action | MK | Resolved | AD | 2016-12-30
58 | 2016-12-12 | 51 | Commercial considerations | Commercial Considerations | Comments on commercial approach and implementation please send ahead for workgroup review | Action | MK | Resolved | All | 2017-01-24
59 | 2017-01-24 | 52 | Workplan | Workplan | RoCoF to be raised during the February meeting | Point to note | GS | Active | GS | 2017-02-01 | To be included on the agenda for February
60 | 2017-01-24 | 52 | Workplan | Assess impact on Vector shift | Query as to whether this still needs to be carried out - 2.11C (assessment of Vector Shift relay) |  | GS | Active | GS
61 | 2017-01-24 | 52 | Workplan | Research | AD's assessment of technologies as requested by the W/G at end of 2016 to be carried out and completed by end of April | Action | AD | Active | AD | 2017-04-30 | AD ready to begin work. Research should take 2 months once plan is signed off and approved National Grid priortiy is 2.13A assessment of relative risk VS and RoCoF For reference: 213.C needs to be covered in AD's research
62 | 2017-01-24 | 52 | Vector Shift | Simulation and Research | Action to update research carried out by National Grid at the next Workgroup meeting in Feb 2017; please refer to the document authored by PS | Action | All | Resolved | PS | 2017-02-28 | PS proposed two questions following the presentation: What do the w/g count as a suitable number of sites assessed to make a confident decision? Is this what was expected? ML would like to see assessment around North Midlands / South Yorkshire and near Birmingham - central network rather than only the peripheries MK relay behaviiour - anything that can be used to compare the wave forms IK 132kw and 33kw to be assessed too ? Spread of the angle to be included in the assessment too - referencing case A and case B
63 | 2017-01-24 | 52 | Vector Shift Study Update | Vector Shift | EB to circulate the list of questions to workgroup and the report again to workgroup | Action | MK | Resolved | EB | ASAP
64 | 2017-01-24 | 52 | Vector Shift Study Update | Vector Shift | All to confirm list of questions complete etc | Action | MK | Resolved | ALL | 2017-02-01
65 | 2017-01-24 | 52 | Facilitating implementation | Commercial Considerations | MK and GS to propose to senior stakeholders in the DNO and National Grid that TNUOS should be used as a mechanism to gain payment for the proposed solution: Scope of the workgroup is to propose a solution and recommendation for next steps Regulatory and procurement project management on how to progress this will be the focus of this discussion | Action | MK | Resolved | MK/GS | 2017-03-01 | MK / GS Will need to liaise with Ofgem with regards potential license changes, however there is an acknowledgement of the restrictions on scope. MK and GS to present to ENFG?
66 | 2017-01-24 | 52 | Facilitating implementation | Commercial Considerations | All to provide any further comments on the paper. | Action | MK | Active | ALL | 2017-02-08
67 | 2017-01-24 | 52 | Facilitating implementation | Commercial Considerations | Workgroup to submit any additional comments to MK / EB regarding the discussion surrounding the commercial recommendations. | Action | MK | Active | MK | 2017-02-07 | Overall there is a cost drive to do this; however the funding to commit to doing the work is the outstanding issue. The Workgroup's scope is based around highlighting the tehcnical specification
68 | 2017-02-28 | 53 | Study Work Scenarios | Scenario reports | Look at what Vector Shift occurs on Fault Clearance | Action | MK | Active | PS | 2017-03-21 | From our analysis the largest vector shift is when the fault occurs and not on fault clearance.
69 | 2017-02-28 | 53 | Study Work Scenarios | Scenario reports | Workgroup require more wave forms to include in further research in collaboration with Adam Dysko relay's performance | Action | MK | Active | PS | 2017-03-21 | Sent waveforms to Adam Dysko
70 | 2017-02-28 | 53 | Study Work Scenarios | Scenario reports | Incidents and impacts on the system when these events occur | Action | MK | Active | GS | 2017-03-21
71 | 2017-02-28 | 53 | ComAp relay investigations | ComAp relay investigations | MK, ML to discuss way forward for ComAp relay with Steve Cox and David Spillet. | Action | MK | Active | MK | 2017-03-21 | This may well need to be presented at Distribution Code Panel.
72 | 2017-02-28 | 53 | ComAp relay investigations | ComAp relay investigations | DNOs to establish numbers of ComAp relays fitted in RoCoF mode to >5MW generators SINCE 1/8/14. | Action | MK | Active | DNOs | 2017-04-30
73 | 2017-02-28 | 53 | Presentation of the GRS/MK slides for ENFG on WG conclusions and next steps | ENFG | MK / GS to update with a summary re. 40,000 sites and the Workgroup assumptions / recommendations re. cost recovery via TNuOS etc and then present to the ENFG | Action | MK | Active | MK/GS | 2017-03-21
| 2017-02-28 | 53 | Case for Change (CBA) update: a) RoCoF and b) Vector Shift | Case for Change (CBA) update: a) RoCoF and b) Vector Shift | GS to include information in the Workgroup report | Point to note | MK | Active | GS | 2017-03-21
| 2017-02-28 | 53
| 2017-02-28 | 53
| 2017-02-28 | 53
| 2017-02-28 | 53
| 2017-02-28 | 53
| 2017-02-28 | 53

## Decision Tracker
GC0048-C EU Coordination Group - Decision Tracker
Owner | Richard Woodward
Meeting Date | Meeting No. | Decision Point
Workgroup Preference:
Name | Organisation | Vote
Mike Kay | ENA
Richard Woodward | NGET SO
Greg Middleton | Deepsea Electronics
John Ruddock | Deepsea Electronics
Graham Stein | NGET SO
Miguel Bernardo | UKPN
Joe Duddy | RES
Campbell McDonald | SSE Generation
Jacob Allinson | RWE
Sam Turner | NPG
Michael Doering | Ecofys
Ioannis Koutsokeras | SP Energy Networks
Martin Lee | SSE Distribution
Honor Hynes | NGET SO
Ellen Bishop | NGET SO
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0

## Sheet1 (hidden)
Active | Point to note | Yes
On Hold | Risk | No
Urgent | Action | Abstain
Resolved | Decision

## Attendance Tracker (hidden)
GC0048-C EU Coordination Group - Workgroup Attendance Tracker
Owner: | Richard Woodward
Name | Organisation | Role | Meeting 41 17-05-16 | Meeting 42 29-06-16 | Meeting 43 00-07-16 | Meeting 44 29-09-16 | Meeting 44 29-09-16 | Meeting 46 15-11-16 | Meeting 47 15-11-16 | Meeting 48 15-11-16 | Meeting 49 15-11-16
Mike Kay | ENA | Chair | Y | Y | Y | Y | Y | Y | Y | Y | Y
Richard Woodward | NGET SO | Technical Secretary | Y | N | Y | N | N | N | N | N | N
Greg Middleton | Deepsea Electronics | WG Member | Y | Y |  | Y | Y | Y | Y | Y | Y
John Ruddock | Deepsea Electronics | WG Member | Y | N
Graham Stein | NGET SO | WG Member | Y | Y | Y | Y | Y | Y | Y | Y | Y
Miguel Bernardo | UKPN | WG Member | Y | N
Joe Duddy | RES | WG Member | Y | Y
Campbell McDonald | SSE Generation | WG Member | Y | Y |  | Y | Y | N * | N * | N * | N *
Jacob Allinson | RWE | WG Member | Y | Y |  | Y | Y | Y | Y | Y | Y
Sam Turner | NPG | WG Member | Y | Y
Michael Doering | Ecofys | Presenter | Y | N
Ioannis Koutsokeras | SP Energy Networks | WG Member | Y | Y |  | Y | Y | Y | Y | Y | Y
Martin Lee | SSE Distribution | WG Member | Y | Y |  | Y | Y | Y | Y | Y | Y
Andy Hood | WPD | WG Member |  | Y |  | N | N | N | N | N | N
Jonny Pollock | NIE Networks | WG Member |  | Y |  | N | N | N | N | N | N
Honor Hynes | NGET SO | Technical Secretary |  | Y |  | N | N | N | N | N | N
Ellen Bishop | NGET SO | Technical Secretary |  |  |  | Y | Y | Y | Y | Y | Y