## Notes
Subject | Notes
System inertia: method of calculation | H=(f*∆P)/(2*RoCoF) H is system inertia; f is the starting frequency; ∆P is the system imbalance; RoCoF is the rate of change of frequency; Note that smaller losses will have less accurate system inertia calculations
RoCoF: method of calculation | RoCoF=(f_500ms-f_0ms)/500ms RoCoF is calculated using 500ms sliding window. RoCoF is the rate of change of frequency; f is the frequency; Note that smaller losses will have less accurate ROCOF calculations
Voltage Dip | Transient Voltage Dip with loss % and duration measured at the local substation
'Immediately before the Significant Event' | The starting frequency indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.
'Immediately after the Significant Event' | The maximum frequency deviation indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.

## Report
|  |  |  | (i) the time(s) in hh.mm.ss of the Significant Event and any potentially related occurrences; | (ii) any known or reported loss of Embedded Power Station(s) with locations and ratings where available; | (iii) the Frequency record (in table and graphical format) at <=1 second intervals for 1 minute before and 1 minute after the Significant Event; | (iv) the Frequency (to 2 decimal places) immediately before the Significant Event; | (v) the Frequency (to 2 decimal places) immediately after the Significant Event; | (vi) the maximum rate of change of Frequency recorded during the Significant Event over a specified time period of 500ms; | (vii) where known, the MW of all individual losses or trips related to the Significant Event; |  | (viii) where known, the identity of the Users and Network Operator of all demand losses or trips related to the Significant Event; | (ix) the location of any reported Transmission fault on the network diagram and geographically; | (x) the extent of any voltage dip associated with the Significant Event; | (xi) an estimate of system inertia in MWs at the time of the Significant Event along with how it has been calculated; and | (xii) any other data available that is of value to gain a clearer understanding of the Significant Event and its potential implications; and
Event Ref | Event Name | Notes | Date (Local) | Time (Local) | Loss of Embedded Power Station | Frequency Record | Pre-Event Frequency | Post-Event Frequency | RoCoF over 500ms | Individual Loss | System Imbalance | Demand loss of Users/DNOs related to event | Location of transmission fault | Voltage Dip | System Inertia | Additional data
Event Date-Number | Text | Text | DD/MM/YYYY | hh:mm:ss | MW | Text | Hz | Hz | Hz/s | Text+MW | MW | Text+MW | Text | % | GWs | Text
Event 20191101-1 | Trip of PEHE-1 |  | 2019-11-01 | 5:38 | N/A | Refer to tab 'Event 20191101-1' | 50.089 | 49.89 | -0.038 | 460 | -460 | N/A | N/A | N/A | 303.1703
Event 20191101-2 | Trip of MRWD-1 |  | 2019-11-01 | 11:23 | N/A | Refer to tab 'Event 20191101-2' | 49.955 | 49.835 | -0.032 | 429 | -429 | N/A | N/A | N/A | 334.8546
Event 20191101-3 | Trip of MRWD-1 |  | 2019-11-01 | 18:52 | N/A | Refer to tab 'Event 20191101-3' | 49.979 | 49.851 | -0.039 | 440 | -440 | N/A | N/A | N/A | 281.9328
Event 20191103-1 | Trip of SPLN-1 |  | 2019-11-03 | 4:19 | N/A | Refer to tab 'Event 20191103-1' | 49.984 | 49.768 | -0.027 | 735 | -735 | N/A | N/A | N/A | 680.3378
Event 20191106-1 | Loss of DIDCB-6 | GT2B Tripped | 2019-11-06 | 13:50 | N/A | Refer to tab 'Event 20191107-1' | 50.052 | 49.847 | -0.015 | 650 | -650 | N/A | N/A | N/A | N/A
Event 20191114-1 | Trip of HRTL-1 |  | 2019-11-14 | 5:18 | N/A | Refer to tab 'Event 20191114-1' | 50.086 | 49.838 | -0.06 | 586 | -586 | N/A | N/A | N/A | 244.5866
Event 20191124-1 | Trip of FIDL-3 | Output reduced gradually from 304MW at 15:22 to 0MW at15:49 | 2019-11-24 | 15:23 | N/A | Refer to tab 'Event 20191124-1' | 50.126 | 49.825 | N/A | 304 | -304 | N/A | N/A | N/A | N/A
Event 20191130-2 | Trip of PEMB-21 |  | 2019-11-30 | 22:21 | N/A | Refer to tab 'Event 20191130-1' | 49.882 | 49.804 | -0.036 | 448 | -448 | N/A | N/A | N/A | 310.3769

## Event 20191101-1
In UTC
Date | Time | Freq
2019-11-01 | 5:36 | 50.078
2019-11-01 | 5:36 | 50.081
2019-11-01 | 5:36 | 50.082
2019-11-01 | 5:36 | 50.083
2019-11-01 | 5:36 | 50.082
2019-11-01 | 5:36 | 50.081
2019-11-01 | 5:36 | 50.08
2019-11-01 | 5:36 | 50.079
2019-11-01 | 5:36 | 50.079
2019-11-01 | 5:36 | 50.079
2019-11-01 | 5:36 | 50.078
2019-11-01 | 5:36 | 50.078
2019-11-01 | 5:36 | 50.077
2019-11-01 | 5:36 | 50.077
2019-11-01 | 5:36 | 50.077
2019-11-01 | 5:36 | 50.078
2019-11-01 | 5:36 | 50.078
2019-11-01 | 5:36 | 50.078
2019-11-01 | 5:36 | 50.078
2019-11-01 | 5:36 | 50.079
2019-11-01 | 5:36 | 50.079
2019-11-01 | 5:36 | 50.08
2019-11-01 | 5:36 | 50.082
2019-11-01 | 5:36 | 50.082
2019-11-01 | 5:36 | 50.083
2019-11-01 | 5:36 | 50.083
2019-11-01 | 5:36 | 50.084
2019-11-01 | 5:36 | 50.083
2019-11-01 | 5:36 | 50.085
2019-11-01 | 5:36 | 50.086
2019-11-01 | 5:36 | 50.09
2019-11-01 | 5:37 | 50.092
2019-11-01 | 5:37 | 50.095
2019-11-01 | 5:37 | 50.097
2019-11-01 | 5:37 | 50.099
2019-11-01 | 5:37 | 50.099
2019-11-01 | 5:37 | 50.098
2019-11-01 | 5:37 | 50.098
2019-11-01 | 5:37 | 50.097
2019-11-01 | 5:37 | 50.096
2019-11-01 | 5:37 | 50.094
2019-11-01 | 5:37 | 50.094
2019-11-01 | 5:37 | 50.093
2019-11-01 | 5:37 | 50.091
2019-11-01 | 5:37 | 50.089
2019-11-01 | 5:37 | 50.088
2019-11-01 | 5:37 | 50.089
2019-11-01 | 5:37 | 50.09
2019-11-01 | 5:37 | 50.091
2019-11-01 | 5:37 | 50.092
2019-11-01 | 5:37 | 50.09
2019-11-01 | 5:37 | 50.09
2019-11-01 | 5:37 | 50.09
2019-11-01 | 5:37 | 50.089
2019-11-01 | 5:37 | 50.09
2019-11-01 | 5:37 | 50.09
2019-11-01 | 5:37 | 50.091
2019-11-01 | 5:37 | 50.09
2019-11-01 | 5:37 | 50.092
2019-11-01 | 5:37 | 50.093
2019-11-01 | 5:37 | 50.093
2019-11-01 | 5:37 | 50.094
2019-11-01 | 5:37 | 50.092
2019-11-01 | 5:37 | 50.091
2019-11-01 | 5:37 | 50.09
2019-11-01 | 5:37 | 50.089
2019-11-01 | 5:37 | 50.089
2019-11-01 | 5:37 | 50.089
2019-11-01 | 5:37 | 50.09
2019-11-01 | 5:37 | 50.091
2019-11-01 | 5:37 | 50.091
2019-11-01 | 5:37 | 50.089
2019-11-01 | 5:37 | 50.089
2019-11-01 | 5:37 | 50.09
2019-11-01 | 5:37 | 50.091
2019-11-01 | 5:37 | 50.092
2019-11-01 | 5:37 | 50.093
2019-11-01 | 5:37 | 50.092
2019-11-01 | 5:37 | 50.092
2019-11-01 | 5:37 | 50.092
2019-11-01 | 5:37 | 50.092
2019-11-01 | 5:37 | 50.09
2019-11-01 | 5:37 | 50.088
2019-11-01 | 5:37 | 50.088
2019-11-01 | 5:37 | 50.088
2019-11-01 | 5:37 | 50.087
2019-11-01 | 5:37 | 50.087
2019-11-01 | 5:37 | 50.086
2019-11-01 | 5:37 | 50.085
2019-11-01 | 5:37 | 50.085
2019-11-01 | 5:38 | 50.084
2019-11-01 | 5:38 | 50.084
2019-11-01 | 5:38 | 50.083
2019-11-01 | 5:38 | 50.082
2019-11-01 | 5:38 | 50.081
2019-11-01 | 5:38 | 50.08
2019-11-01 | 5:38 | 50.079
2019-11-01 | 5:38 | 50.08
2019-11-01 | 5:38 | 50.079
2019-11-01 | 5:38 | 50.079
2019-11-01 | 5:38 | 50.079
2019-11-01 | 5:38 | 50.081
2019-11-01 | 5:38 | 50.083
2019-11-01 | 5:38 | 50.085
2019-11-01 | 5:38 | 50.085
2019-11-01 | 5:38 | 50.086
2019-11-01 | 5:38 | 50.087
2019-11-01 | 5:38 | 50.088
2019-11-01 | 5:38 | 50.087
2019-11-01 | 5:38 | 50.089
2019-11-01 | 5:38 | 50.089
2019-11-01 | 5:38 | 50.091
2019-11-01 | 5:38 | 50.089
2019-11-01 | 5:38 | 50.087
2019-11-01 | 5:38 | 50.084
2019-11-01 | 5:38 | 50.072
2019-11-01 | 5:38 | 50.046
2019-11-01 | 5:38 | 50.024
2019-11-01 | 5:38 | 50.01
2019-11-01 | 5:38 | 50.003
2019-11-01 | 5:38 | 49.998
2019-11-01 | 5:38 | 49.998
2019-11-01 | 5:38 | 49.998
2019-11-01 | 5:38 | 49.999
2019-11-01 | 5:38 | 50.002
2019-11-01 | 5:38 | 50.005
2019-11-01 | 5:38 | 50.008
2019-11-01 | 5:38 | 50.012
2019-11-01 | 5:38 | 50.015
2019-11-01 | 5:38 | 50.018
2019-11-01 | 5:38 | 50.019
2019-11-01 | 5:38 | 50.018
2019-11-01 | 5:38 | 50.018
2019-11-01 | 5:38 | 50.018
2019-11-01 | 5:38 | 50.016
2019-11-01 | 5:38 | 50.014
2019-11-01 | 5:38 | 50.011
2019-11-01 | 5:38 | 50.008
2019-11-01 | 5:38 | 50.004
2019-11-01 | 5:38 | 50.001
2019-11-01 | 5:38 | 49.999
2019-11-01 | 5:38 | 49.997
2019-11-01 | 5:38 | 49.997
2019-11-01 | 5:38 | 49.998
2019-11-01 | 5:38 | 49.999
2019-11-01 | 5:38 | 50
2019-11-01 | 5:38 | 49.997
2019-11-01 | 5:38 | 49.993
2019-11-01 | 5:38 | 49.989
2019-11-01 | 5:38 | 49.985
2019-11-01 | 5:38 | 49.982
2019-11-01 | 5:39 | 49.981
2019-11-01 | 5:39 | 49.98
2019-11-01 | 5:39 | 49.979
2019-11-01 | 5:39 | 49.979
2019-11-01 | 5:39 | 49.979
2019-11-01 | 5:39 | 49.98
2019-11-01 | 5:39 | 49.981
2019-11-01 | 5:39 | 49.981
2019-11-01 | 5:39 | 49.982
2019-11-01 | 5:39 | 49.984
2019-11-01 | 5:39 | 49.986
2019-11-01 | 5:39 | 49.989
2019-11-01 | 5:39 | 49.99
2019-11-01 | 5:39 | 49.991
2019-11-01 | 5:39 | 49.992
2019-11-01 | 5:39 | 49.991
2019-11-01 | 5:39 | 49.989
2019-11-01 | 5:39 | 49.988
2019-11-01 | 5:39 | 49.988
2019-11-01 | 5:39 | 49.989
2019-11-01 | 5:39 | 49.988
2019-11-01 | 5:39 | 49.988
2019-11-01 | 5:39 | 49.986
2019-11-01 | 5:39 | 49.986
2019-11-01 | 5:39 | 49.984
2019-11-01 | 5:39 | 49.982
2019-11-01 | 5:39 | 49.98
2019-11-01 | 5:39 | 49.978
2019-11-01 | 5:39 | 49.977
2019-11-01 | 5:39 | 49.974
2019-11-01 | 5:39 | 49.973
2019-11-01 | 5:39 | 49.972
2019-11-01 | 5:39 | 49.971
2019-11-01 | 5:39 | 49.972
2019-11-01 | 5:39 | 49.971
2019-11-01 | 5:39 | 49.972
2019-11-01 | 5:39 | 49.971
2019-11-01 | 5:39 | 49.972
2019-11-01 | 5:39 | 49.971
2019-11-01 | 5:39 | 49.969
2019-11-01 | 5:39 | 49.967
2019-11-01 | 5:39 | 49.966
2019-11-01 | 5:39 | 49.967
2019-11-01 | 5:39 | 49.968
2019-11-01 | 5:39 | 49.969
2019-11-01 | 5:39 | 49.968
2019-11-01 | 5:39 | 49.968
2019-11-01 | 5:39 | 49.968
2019-11-01 | 5:39 | 49.968
2019-11-01 | 5:39 | 49.967
2019-11-01 | 5:39 | 49.967
2019-11-01 | 5:39 | 49.967
2019-11-01 | 5:39 | 49.966
2019-11-01 | 5:39 | 49.965
2019-11-01 | 5:39 | 49.963
2019-11-01 | 5:39 | 49.964
2019-11-01 | 5:39 | 49.965
2019-11-01 | 5:39 | 49.966
2019-11-01 | 5:39 | 49.965
2019-11-01 | 5:40 | 49.967
2019-11-01 | 5:40 | 49.969
2019-11-01 | 5:40 | 49.97
2019-11-01 | 5:40 | 49.971
2019-11-01 | 5:40 | 49.971
2019-11-01 | 5:40 | 49.971
2019-11-01 | 5:40 | 49.971
2019-11-01 | 5:40 | 49.971
2019-11-01 | 5:40 | 49.971
2019-11-01 | 5:40 | 49.972
2019-11-01 | 5:40 | 49.974
2019-11-01 | 5:40 | 49.976
2019-11-01 | 5:40 | 49.978
2019-11-01 | 5:40 | 49.979
2019-11-01 | 5:40 | 49.98
2019-11-01 | 5:40 | 49.98
2019-11-01 | 5:40 | 49.981
2019-11-01 | 5:40 | 49.981
2019-11-01 | 5:40 | 49.98
2019-11-01 | 5:40 | 49.978
2019-11-01 | 5:40 | 49.976
2019-11-01 | 5:40 | 49.974
2019-11-01 | 5:40 | 49.972
2019-11-01 | 5:40 | 49.971
2019-11-01 | 5:40 | 49.97
2019-11-01 | 5:40 | 49.968
2019-11-01 | 5:40 | 49.965
2019-11-01 | 5:40 | 49.962
2019-11-01 | 5:40 | 49.959
2019-11-01 | 5:40 | 49.955
2019-11-01 | 5:40 | 49.953
2019-11-01 | 5:40 | 49.953
2019-11-01 | 5:40 | 49.952
2019-11-01 | 5:40 | 49.952
2019-11-01 | 5:40 | 49.953
2019-11-01 | 5:40 | 49.952
2019-11-01 | 5:40 | 49.951
2019-11-01 | 5:40 | 49.949
2019-11-01 | 5:40 | 49.946
2019-11-01 | 5:40 | 49.944
2019-11-01 | 5:40 | 49.943
2019-11-01 | 5:40 | 49.943
2019-11-01 | 5:40 | 49.942
2019-11-01 | 5:40 | 49.942
2019-11-01 | 5:40 | 49.942
2019-11-01 | 5:40 | 49.941
2019-11-01 | 5:40 | 49.941
2019-11-01 | 5:40 | 49.942
2019-11-01 | 5:40 | 49.945
2019-11-01 | 5:40 | 49.945
2019-11-01 | 5:40 | 49.946
2019-11-01 | 5:40 | 49.949
2019-11-01 | 5:40 | 49.951
2019-11-01 | 5:40 | 49.954
2019-11-01 | 5:40 | 49.956
2019-11-01 | 5:40 | 49.958
2019-11-01 | 5:40 | 49.958
2019-11-01 | 5:40 | 49.959
2019-11-01 | 5:40 | 49.959
2019-11-01 | 5:40 | 49.96
2019-11-01 | 5:40 | 49.962
2019-11-01 | 5:41 | 49.961
2019-11-01 | 5:41 | 49.961
2019-11-01 | 5:41 | 49.96
2019-11-01 | 5:41 | 49.958
2019-11-01 | 5:41 | 49.955
2019-11-01 | 5:41 | 49.953
2019-11-01 | 5:41 | 49.951
2019-11-01 | 5:41 | 49.949
2019-11-01 | 5:41 | 49.947
2019-11-01 | 5:41 | 49.944
2019-11-01 | 5:41 | 49.943
2019-11-01 | 5:41 | 49.943
2019-11-01 | 5:41 | 49.944
2019-11-01 | 5:41 | 49.945
2019-11-01 | 5:41 | 49.945
2019-11-01 | 5:41 | 49.946
2019-11-01 | 5:41 | 49.946
2019-11-01 | 5:41 | 49.946
2019-11-01 | 5:41 | 49.948
2019-11-01 | 5:41 | 49.949
2019-11-01 | 5:41 | 49.952
2019-11-01 | 5:41 | 49.951
2019-11-01 | 5:41 | 49.95
2019-11-01 | 5:41 | 49.95
2019-11-01 | 5:41 | 49.949
2019-11-01 | 5:41 | 49.949
2019-11-01 | 5:41 | 49.946
2019-11-01 | 5:41 | 49.945
2019-11-01 | 5:41 | 49.942
2019-11-01 | 5:41 | 49.939
2019-11-01 | 5:41 | 49.937
2019-11-01 | 5:41 | 49.934
2019-11-01 | 5:41 | 49.931
2019-11-01 | 5:41 | 49.929
2019-11-01 | 5:41 | 49.928
2019-11-01 | 5:41 | 49.927
2019-11-01 | 5:41 | 49.927
2019-11-01 | 5:41 | 49.928
2019-11-01 | 5:41 | 49.926
2019-11-01 | 5:41 | 49.925
2019-11-01 | 5:41 | 49.926
2019-11-01 | 5:41 | 49.927
2019-11-01 | 5:41 | 49.929
2019-11-01 | 5:41 | 49.932
2019-11-01 | 5:41 | 49.936
2019-11-01 | 5:41 | 49.939
2019-11-01 | 5:41 | 49.943
2019-11-01 | 5:41 | 49.945
2019-11-01 | 5:41 | 49.946
2019-11-01 | 5:41 | 49.944
2019-11-01 | 5:41 | 49.943
2019-11-01 | 5:41 | 49.942
2019-11-01 | 5:41 | 49.935
2019-11-01 | 5:41 | 49.931
2019-11-01 | 5:41 | 49.925
2019-11-01 | 5:41 | 49.921
2019-11-01 | 5:41 | 49.92
2019-11-01 | 5:41 | 49.919
2019-11-01 | 5:41 | 49.919
2019-11-01 | 5:42 | 49.92
2019-11-01 | 5:42 | 49.922
2019-11-01 | 5:42 | 49.924
2019-11-01 | 5:42 | 49.923
2019-11-01 | 5:42 | 49.924
2019-11-01 | 5:42 | 49.925
2019-11-01 | 5:42 | 49.925
2019-11-01 | 5:42 | 49.926
2019-11-01 | 5:42 | 49.926
2019-11-01 | 5:42 | 49.928
2019-11-01 | 5:42 | 49.931
2019-11-01 | 5:42 | 49.932
2019-11-01 | 5:42 | 49.934
2019-11-01 | 5:42 | 49.934
2019-11-01 | 5:42 | 49.933
2019-11-01 | 5:42 | 49.932
2019-11-01 | 5:42 | 49.932
2019-11-01 | 5:42 | 49.933
2019-11-01 | 5:42 | 49.932
2019-11-01 | 5:42 | 49.935
2019-11-01 | 5:42 | 49.937
2019-11-01 | 5:42 | 49.937
2019-11-01 | 5:42 | 49.937
2019-11-01 | 5:42 | 49.935
2019-11-01 | 5:42 | 49.936
2019-11-01 | 5:42 | 49.937
2019-11-01 | 5:42 | 49.937
2019-11-01 | 5:42 | 49.938
2019-11-01 | 5:42 | 49.937
2019-11-01 | 5:42 | 49.937
2019-11-01 | 5:42 | 49.937
2019-11-01 | 5:42 | 49.937
2019-11-01 | 5:42 | 49.935
2019-11-01 | 5:42 | 49.933
2019-11-01 | 5:42 | 49.929
2019-11-01 | 5:42 | 49.925
2019-11-01 | 5:42 | 49.921
2019-11-01 | 5:42 | 49.918
2019-11-01 | 5:42 | 49.916
2019-11-01 | 5:42 | 49.915
2019-11-01 | 5:42 | 49.915
2019-11-01 | 5:42 | 49.915
2019-11-01 | 5:42 | 49.916
2019-11-01 | 5:42 | 49.919
2019-11-01 | 5:42 | 49.921
2019-11-01 | 5:42 | 49.926
2019-11-01 | 5:42 | 49.93
2019-11-01 | 5:42 | 49.934
2019-11-01 | 5:42 | 49.936
2019-11-01 | 5:42 | 49.937
2019-11-01 | 5:42 | 49.937
2019-11-01 | 5:42 | 49.938
2019-11-01 | 5:42 | 49.938
2019-11-01 | 5:42 | 49.938
2019-11-01 | 5:42 | 49.938
2019-11-01 | 5:42 | 49.937
2019-11-01 | 5:42 | 49.936
2019-11-01 | 5:42 | 49.933
2019-11-01 | 5:42 | 49.932
2019-11-01 | 5:42 | 49.93
2019-11-01 | 5:42 | 49.927
2019-11-01 | 5:43 | 49.925
2019-11-01 | 5:43 | 49.924
2019-11-01 | 5:43 | 49.923
2019-11-01 | 5:43 | 49.923
2019-11-01 | 5:43 | 49.923
2019-11-01 | 5:43 | 49.924
2019-11-01 | 5:43 | 49.922
2019-11-01 | 5:43 | 49.922
2019-11-01 | 5:43 | 49.922
2019-11-01 | 5:43 | 49.923
2019-11-01 | 5:43 | 49.923
2019-11-01 | 5:43 | 49.922
2019-11-01 | 5:43 | 49.921
2019-11-01 | 5:43 | 49.921
2019-11-01 | 5:43 | 49.922
2019-11-01 | 5:43 | 49.92
2019-11-01 | 5:43 | 49.92
2019-11-01 | 5:43 | 49.92
2019-11-01 | 5:43 | 49.92
2019-11-01 | 5:43 | 49.92
2019-11-01 | 5:43 | 49.919
2019-11-01 | 5:43 | 49.919
2019-11-01 | 5:43 | 49.918
2019-11-01 | 5:43 | 49.918
2019-11-01 | 5:43 | 49.916
2019-11-01 | 5:43 | 49.916
2019-11-01 | 5:43 | 49.915
2019-11-01 | 5:43 | 49.914
2019-11-01 | 5:43 | 49.912
2019-11-01 | 5:43 | 49.909
2019-11-01 | 5:43 | 49.91
2019-11-01 | 5:43 | 49.91
2019-11-01 | 5:43 | 49.911
2019-11-01 | 5:43 | 49.913
2019-11-01 | 5:43 | 49.914
2019-11-01 | 5:43 | 49.915
2019-11-01 | 5:43 | 49.915
2019-11-01 | 5:43 | 49.916
2019-11-01 | 5:43 | 49.917
2019-11-01 | 5:43 | 49.918
2019-11-01 | 5:43 | 49.918
2019-11-01 | 5:43 | 49.917
2019-11-01 | 5:43 | 49.914
2019-11-01 | 5:43 | 49.912
2019-11-01 | 5:43 | 49.91
2019-11-01 | 5:43 | 49.907
2019-11-01 | 5:43 | 49.903
2019-11-01 | 5:43 | 49.899
2019-11-01 | 5:43 | 49.898
2019-11-01 | 5:43 | 49.896
2019-11-01 | 5:43 | 49.896
2019-11-01 | 5:43 | 49.894
2019-11-01 | 5:43 | 49.894
2019-11-01 | 5:43 | 49.895
2019-11-01 | 5:43 | 49.896
2019-11-01 | 5:43 | 49.897
2019-11-01 | 5:43 | 49.899
2019-11-01 | 5:43 | 49.901
2019-11-01 | 5:43 | 49.902
2019-11-01 | 5:44 | 49.902
2019-11-01 | 5:44 | 49.902
2019-11-01 | 5:44 | 49.902
2019-11-01 | 5:44 | 49.901
2019-11-01 | 5:44 | 49.902
2019-11-01 | 5:44 | 49.903
2019-11-01 | 5:44 | 49.906
2019-11-01 | 5:44 | 49.906
2019-11-01 | 5:44 | 49.907
2019-11-01 | 5:44 | 49.907
2019-11-01 | 5:44 | 49.906
2019-11-01 | 5:44 | 49.906
2019-11-01 | 5:44 | 49.906
2019-11-01 | 5:44 | 49.904
2019-11-01 | 5:44 | 49.903
2019-11-01 | 5:44 | 49.9
2019-11-01 | 5:44 | 49.898
2019-11-01 | 5:44 | 49.896
2019-11-01 | 5:44 | 49.895
2019-11-01 | 5:44 | 49.893
2019-11-01 | 5:44 | 49.892
2019-11-01 | 5:44 | 49.893
2019-11-01 | 5:44 | 49.893
2019-11-01 | 5:44 | 49.892
2019-11-01 | 5:44 | 49.893
2019-11-01 | 5:44 | 49.894
2019-11-01 | 5:44 | 49.895
2019-11-01 | 5:44 | 49.897
2019-11-01 | 5:44 | 49.897
2019-11-01 | 5:44 | 49.899
2019-11-01 | 5:44 | 49.901
2019-11-01 | 5:44 | 49.902
2019-11-01 | 5:44 | 49.901
2019-11-01 | 5:44 | 49.902
2019-11-01 | 5:44 | 49.902
2019-11-01 | 5:44 | 49.902
2019-11-01 | 5:44 | 49.904
2019-11-01 | 5:44 | 49.905
2019-11-01 | 5:44 | 49.905
2019-11-01 | 5:44 | 49.905
2019-11-01 | 5:44 | 49.903
2019-11-01 | 5:44 | 49.902
2019-11-01 | 5:44 | 49.9
2019-11-01 | 5:44 | 49.899
2019-11-01 | 5:44 | 49.9
2019-11-01 | 5:44 | 49.899
2019-11-01 | 5:44 | 49.898
2019-11-01 | 5:44 | 49.898
2019-11-01 | 5:44 | 49.897
2019-11-01 | 5:44 | 49.898
2019-11-01 | 5:44 | 49.896
2019-11-01 | 5:44 | 49.894
2019-11-01 | 5:44 | 49.894
2019-11-01 | 5:44 | 49.893
2019-11-01 | 5:44 | 49.893
2019-11-01 | 5:44 | 49.893
2019-11-01 | 5:44 | 49.894
2019-11-01 | 5:44 | 49.897
2019-11-01 | 5:44 | 49.899
2019-11-01 | 5:44 | 49.902
2019-11-01 | 5:44 | 49.906
2019-11-01 | 5:45 | 49.909
2019-11-01 | 5:45 | 49.913
2019-11-01 | 5:45 | 49.916
2019-11-01 | 5:45 | 49.92
2019-11-01 | 5:45 | 49.922
2019-11-01 | 5:45 | 49.922
2019-11-01 | 5:45 | 49.926
2019-11-01 | 5:45 | 49.929
2019-11-01 | 5:45 | 49.93
2019-11-01 | 5:45 | 49.931
2019-11-01 | 5:45 | 49.931
2019-11-01 | 5:45 | 49.931
2019-11-01 | 5:45 | 49.93
2019-11-01 | 5:45 | 49.931
2019-11-01 | 5:45 | 49.93
2019-11-01 | 5:45 | 49.929
2019-11-01 | 5:45 | 49.927
2019-11-01 | 5:45 | 49.928
2019-11-01 | 5:45 | 49.928
2019-11-01 | 5:45 | 49.927
2019-11-01 | 5:45 | 49.926
2019-11-01 | 5:45 | 49.925
2019-11-01 | 5:45 | 49.924
2019-11-01 | 5:45 | 49.922
2019-11-01 | 5:45 | 49.922
2019-11-01 | 5:45 | 49.921
2019-11-01 | 5:45 | 49.923
2019-11-01 | 5:45 | 49.923
2019-11-01 | 5:45 | 49.923
2019-11-01 | 5:45 | 49.924
2019-11-01 | 5:45 | 49.925
2019-11-01 | 5:45 | 49.924
2019-11-01 | 5:45 | 49.924
2019-11-01 | 5:45 | 49.925
2019-11-01 | 5:45 | 49.925
2019-11-01 | 5:45 | 49.925
2019-11-01 | 5:45 | 49.924
2019-11-01 | 5:45 | 49.923
2019-11-01 | 5:45 | 49.922
2019-11-01 | 5:45 | 49.923
2019-11-01 | 5:45 | 49.924
2019-11-01 | 5:45 | 49.923
2019-11-01 | 5:45 | 49.922
2019-11-01 | 5:45 | 49.921
2019-11-01 | 5:45 | 49.92
2019-11-01 | 5:45 | 49.919
2019-11-01 | 5:45 | 49.918
2019-11-01 | 5:45 | 49.917
2019-11-01 | 5:45 | 49.916
2019-11-01 | 5:45 | 49.917
2019-11-01 | 5:45 | 49.917
2019-11-01 | 5:45 | 49.918
2019-11-01 | 5:45 | 49.916
2019-11-01 | 5:45 | 49.915
2019-11-01 | 5:45 | 49.916
2019-11-01 | 5:45 | 49.919
2019-11-01 | 5:45 | 49.921
2019-11-01 | 5:45 | 49.921
2019-11-01 | 5:45 | 49.921
2019-11-01 | 5:46 | 49.92
2019-11-01 | 5:46 | 49.922
2019-11-01 | 5:46 | 49.923
2019-11-01 | 5:46 | 49.922
2019-11-01 | 5:46 | 49.921
2019-11-01 | 5:46 | 49.92
2019-11-01 | 5:46 | 49.92
2019-11-01 | 5:46 | 49.918
2019-11-01 | 5:46 | 49.918
2019-11-01 | 5:46 | 49.919
2019-11-01 | 5:46 | 49.921
2019-11-01 | 5:46 | 49.923
2019-11-01 | 5:46 | 49.925
2019-11-01 | 5:46 | 49.927
2019-11-01 | 5:46 | 49.929
2019-11-01 | 5:46 | 49.931
2019-11-01 | 5:46 | 49.933
2019-11-01 | 5:46 | 49.934
2019-11-01 | 5:46 | 49.933
2019-11-01 | 5:46 | 49.932
2019-11-01 | 5:46 | 49.931
2019-11-01 | 5:46 | 49.93
2019-11-01 | 5:46 | 49.928
2019-11-01 | 5:46 | 49.925
2019-11-01 | 5:46 | 49.922
2019-11-01 | 5:46 | 49.921
2019-11-01 | 5:46 | 49.921
2019-11-01 | 5:46 | 49.925
2019-11-01 | 5:46 | 49.928
2019-11-01 | 5:46 | 49.929
2019-11-01 | 5:46 | 49.929
2019-11-01 | 5:46 | 49.931
2019-11-01 | 5:46 | 49.931
2019-11-01 | 5:46 | 49.93
2019-11-01 | 5:46 | 49.927
2019-11-01 | 5:46 | 49.925
2019-11-01 | 5:46 | 49.922
2019-11-01 | 5:46 | 49.919
2019-11-01 | 5:46 | 49.918
2019-11-01 | 5:46 | 49.918
2019-11-01 | 5:46 | 49.919
2019-11-01 | 5:46 | 49.92
2019-11-01 | 5:46 | 49.922
2019-11-01 | 5:46 | 49.923
2019-11-01 | 5:46 | 49.923
2019-11-01 | 5:46 | 49.925
2019-11-01 | 5:46 | 49.925
2019-11-01 | 5:46 | 49.925
2019-11-01 | 5:46 | 49.924
2019-11-01 | 5:46 | 49.924
2019-11-01 | 5:46 | 49.924
2019-11-01 | 5:46 | 49.927
2019-11-01 | 5:46 | 49.928
2019-11-01 | 5:46 | 49.931
2019-11-01 | 5:46 | 49.935
2019-11-01 | 5:46 | 49.94
2019-11-01 | 5:46 | 49.943
2019-11-01 | 5:46 | 49.944
2019-11-01 | 5:46 | 49.944
2019-11-01 | 5:46 | 49.943
2019-11-01 | 5:46 | 49.943
2019-11-01 | 5:47 | 49.941
2019-11-01 | 5:47 | 49.939
2019-11-01 | 5:47 | 49.935
2019-11-01 | 5:47 | 49.93
2019-11-01 | 5:47 | 49.929
2019-11-01 | 5:47 | 49.928
2019-11-01 | 5:47 | 49.928
2019-11-01 | 5:47 | 49.928
2019-11-01 | 5:47 | 49.928
2019-11-01 | 5:47 | 49.929
2019-11-01 | 5:47 | 49.93
2019-11-01 | 5:47 | 49.933
2019-11-01 | 5:47 | 49.933
2019-11-01 | 5:47 | 49.932
2019-11-01 | 5:47 | 49.933
2019-11-01 | 5:47 | 49.937
2019-11-01 | 5:47 | 49.939
2019-11-01 | 5:47 | 49.944
2019-11-01 | 5:47 | 49.948
2019-11-01 | 5:47 | 49.949
2019-11-01 | 5:47 | 49.95
2019-11-01 | 5:47 | 49.952
2019-11-01 | 5:47 | 49.953
2019-11-01 | 5:47 | 49.953
2019-11-01 | 5:47 | 49.955
2019-11-01 | 5:47 | 49.955
2019-11-01 | 5:47 | 49.954
2019-11-01 | 5:47 | 49.953
2019-11-01 | 5:47 | 49.953
2019-11-01 | 5:47 | 49.953
2019-11-01 | 5:47 | 49.951
2019-11-01 | 5:47 | 49.949
2019-11-01 | 5:47 | 49.947
2019-11-01 | 5:47 | 49.946
2019-11-01 | 5:47 | 49.944
2019-11-01 | 5:47 | 49.944
2019-11-01 | 5:47 | 49.944
2019-11-01 | 5:47 | 49.945
2019-11-01 | 5:47 | 49.947
2019-11-01 | 5:47 | 49.948
2019-11-01 | 5:47 | 49.949
2019-11-01 | 5:47 | 49.951
2019-11-01 | 5:47 | 49.954
2019-11-01 | 5:47 | 49.96
2019-11-01 | 5:47 | 49.963
2019-11-01 | 5:47 | 49.967
2019-11-01 | 5:47 | 49.968
2019-11-01 | 5:47 | 49.969
2019-11-01 | 5:47 | 49.971
2019-11-01 | 5:47 | 49.971
2019-11-01 | 5:47 | 49.971
2019-11-01 | 5:47 | 49.969
2019-11-01 | 5:47 | 49.968
2019-11-01 | 5:47 | 49.967
2019-11-01 | 5:47 | 49.965
2019-11-01 | 5:47 | 49.963
2019-11-01 | 5:47 | 49.961
2019-11-01 | 5:47 | 49.96
2019-11-01 | 5:47 | 49.958
2019-11-01 | 5:48 | 49.958
2019-11-01 | 5:48 | 49.956
2019-11-01 | 5:48 | 49.952
2019-11-01 | 5:48 | 49.95
2019-11-01 | 5:48 | 49.95
2019-11-01 | 5:48 | 49.949
2019-11-01 | 5:48 | 49.948
2019-11-01 | 5:48 | 49.948
2019-11-01 | 5:48 | 49.948
2019-11-01 | 5:48 | 49.949
2019-11-01 | 5:48 | 49.948
2019-11-01 | 5:48 | 49.948
2019-11-01 | 5:48 | 49.948
2019-11-01 | 5:48 | 49.947
2019-11-01 | 5:48 | 49.947
2019-11-01 | 5:48 | 49.949
2019-11-01 | 5:48 | 49.948
2019-11-01 | 5:48 | 49.949
2019-11-01 | 5:48 | 49.95
2019-11-01 | 5:48 | 49.952
2019-11-01 | 5:48 | 49.956
2019-11-01 | 5:48 | 49.956
2019-11-01 | 5:48 | 49.956
2019-11-01 | 5:48 | 49.956
2019-11-01 | 5:48 | 49.954
2019-11-01 | 5:48 | 49.953
2019-11-01 | 5:48 | 49.954
2019-11-01 | 5:48 | 49.956
2019-11-01 | 5:48 | 49.959
2019-11-01 | 5:48 | 49.961
2019-11-01 | 5:48 | 49.96
2019-11-01 | 5:48 | 49.959
2019-11-01 | 5:48 | 49.959
2019-11-01 | 5:48 | 49.959
2019-11-01 | 5:48 | 49.958
2019-11-01 | 5:48 | 49.956
2019-11-01 | 5:48 | 49.954
2019-11-01 | 5:48 | 49.954
2019-11-01 | 5:48 | 49.954
2019-11-01 | 5:48 | 49.954
2019-11-01 | 5:48 | 49.954
2019-11-01 | 5:48 | 49.954
2019-11-01 | 5:48 | 49.954
2019-11-01 | 5:48 | 49.956
2019-11-01 | 5:48 | 49.959
2019-11-01 | 5:48 | 49.959
2019-11-01 | 5:48 | 49.958
2019-11-01 | 5:48 | 49.958
2019-11-01 | 5:48 | 49.957
2019-11-01 | 5:48 | 49.957
2019-11-01 | 5:48 | 49.955
2019-11-01 | 5:48 | 49.953
2019-11-01 | 5:48 | 49.95
2019-11-01 | 5:48 | 49.948
2019-11-01 | 5:48 | 49.947
2019-11-01 | 5:48 | 49.946
2019-11-01 | 5:48 | 49.946
2019-11-01 | 5:48 | 49.95
2019-11-01 | 5:48 | 49.953
2019-11-01 | 5:48 | 49.957
2019-11-01 | 5:48 | 49.959
2019-11-01 | 5:49 | 49.959
2019-11-01 | 5:49 | 49.96
2019-11-01 | 5:49 | 49.96
2019-11-01 | 5:49 | 49.96
2019-11-01 | 5:49 | 49.961
2019-11-01 | 5:49 | 49.96
2019-11-01 | 5:49 | 49.961
2019-11-01 | 5:49 | 49.96
2019-11-01 | 5:49 | 49.957
2019-11-01 | 5:49 | 49.958
2019-11-01 | 5:49 | 49.959
2019-11-01 | 5:49 | 49.959
2019-11-01 | 5:49 | 49.96
2019-11-01 | 5:49 | 49.96
2019-11-01 | 5:49 | 49.962
2019-11-01 | 5:49 | 49.969
2019-11-01 | 5:49 | 49.971
2019-11-01 | 5:49 | 49.976
2019-11-01 | 5:49 | 49.98
2019-11-01 | 5:49 | 49.985
2019-11-01 | 5:49 | 49.986
2019-11-01 | 5:49 | 49.986
2019-11-01 | 5:49 | 49.986
2019-11-01 | 5:49 | 49.986
2019-11-01 | 5:49 | 49.986
2019-11-01 | 5:49 | 49.985
2019-11-01 | 5:49 | 49.984
2019-11-01 | 5:49 | 49.984
2019-11-01 | 5:49 | 49.984
2019-11-01 | 5:49 | 49.986
2019-11-01 | 5:49 | 49.988
2019-11-01 | 5:49 | 49.988
2019-11-01 | 5:49 | 49.987
2019-11-01 | 5:49 | 49.984
2019-11-01 | 5:49 | 49.983
2019-11-01 | 5:49 | 49.982
2019-11-01 | 5:49 | 49.982
2019-11-01 | 5:49 | 49.979
2019-11-01 | 5:49 | 49.976
2019-11-01 | 5:49 | 49.976
2019-11-01 | 5:49 | 49.973
2019-11-01 | 5:49 | 49.972
2019-11-01 | 5:49 | 49.971
2019-11-01 | 5:49 | 49.971
2019-11-01 | 5:49 | 49.971
2019-11-01 | 5:49 | 49.974
2019-11-01 | 5:49 | 49.977
2019-11-01 | 5:49 | 49.979
2019-11-01 | 5:49 | 49.982
2019-11-01 | 5:49 | 49.986
2019-11-01 | 5:49 | 49.989
2019-11-01 | 5:49 | 49.991
2019-11-01 | 5:49 | 49.991
2019-11-01 | 5:49 | 49.991
2019-11-01 | 5:49 | 49.992
2019-11-01 | 5:49 | 49.993
2019-11-01 | 5:49 | 49.993
2019-11-01 | 5:49 | 49.997
2019-11-01 | 5:49 | 49.999
2019-11-01 | 5:50 | 50.002
2019-11-01 | 5:50 | 50.004
2019-11-01 | 5:50 | 50.008
2019-11-01 | 5:50 | 50.009
2019-11-01 | 5:50 | 50.008
2019-11-01 | 5:50 | 50.006
2019-11-01 | 5:50 | 50.003
2019-11-01 | 5:50 | 50
2019-11-01 | 5:50 | 50
2019-11-01 | 5:50 | 50
2019-11-01 | 5:50 | 50.001
2019-11-01 | 5:50 | 50.001
2019-11-01 | 5:50 | 50.002
2019-11-01 | 5:50 | 50.001
2019-11-01 | 5:50 | 50.001
2019-11-01 | 5:50 | 50
2019-11-01 | 5:50 | 50
2019-11-01 | 5:50 | 49.997
2019-11-01 | 5:50 | 49.994
2019-11-01 | 5:50 | 49.989
2019-11-01 | 5:50 | 49.987
2019-11-01 | 5:50 | 49.983
2019-11-01 | 5:50 | 49.98
2019-11-01 | 5:50 | 49.979
2019-11-01 | 5:50 | 49.98
2019-11-01 | 5:50 | 49.983
2019-11-01 | 5:50 | 49.986
2019-11-01 | 5:50 | 49.99
2019-11-01 | 5:50 | 49.994
2019-11-01 | 5:50 | 49.997

## Event 20191101-2
In UTC
Date | Time | Freq
2019-11-01 | 11:22 | 49.936
2019-11-01 | 11:22 | 49.933
2019-11-01 | 11:22 | 49.931
2019-11-01 | 11:22 | 49.931
2019-11-01 | 11:22 | 49.93
2019-11-01 | 11:22 | 49.931
2019-11-01 | 11:22 | 49.932
2019-11-01 | 11:22 | 49.932
2019-11-01 | 11:22 | 49.934
2019-11-01 | 11:22 | 49.936
2019-11-01 | 11:22 | 49.939
2019-11-01 | 11:22 | 49.941
2019-11-01 | 11:22 | 49.942
2019-11-01 | 11:22 | 49.942
2019-11-01 | 11:22 | 49.943
2019-11-01 | 11:22 | 49.944
2019-11-01 | 11:22 | 49.944
2019-11-01 | 11:22 | 49.945
2019-11-01 | 11:22 | 49.945
2019-11-01 | 11:22 | 49.945
2019-11-01 | 11:22 | 49.944
2019-11-01 | 11:22 | 49.942
2019-11-01 | 11:22 | 49.941
2019-11-01 | 11:22 | 49.938
2019-11-01 | 11:22 | 49.936
2019-11-01 | 11:22 | 49.932
2019-11-01 | 11:22 | 49.932
2019-11-01 | 11:22 | 49.931
2019-11-01 | 11:22 | 49.931
2019-11-01 | 11:22 | 49.934
2019-11-01 | 11:22 | 49.936
2019-11-01 | 11:23 | 49.938
2019-11-01 | 11:23 | 49.94
2019-11-01 | 11:23 | 49.942
2019-11-01 | 11:23 | 49.943
2019-11-01 | 11:23 | 49.943
2019-11-01 | 11:23 | 49.946
2019-11-01 | 11:23 | 49.947
2019-11-01 | 11:23 | 49.945
2019-11-01 | 11:23 | 49.944
2019-11-01 | 11:23 | 49.944
2019-11-01 | 11:23 | 49.945
2019-11-01 | 11:23 | 49.947
2019-11-01 | 11:23 | 49.95
2019-11-01 | 11:23 | 49.951
2019-11-01 | 11:23 | 49.951
2019-11-01 | 11:23 | 49.951
2019-11-01 | 11:23 | 49.952
2019-11-01 | 11:23 | 49.953
2019-11-01 | 11:23 | 49.954
2019-11-01 | 11:23 | 49.953
2019-11-01 | 11:23 | 49.953
2019-11-01 | 11:23 | 49.954
2019-11-01 | 11:23 | 49.956
2019-11-01 | 11:23 | 49.957
2019-11-01 | 11:23 | 49.956
2019-11-01 | 11:23 | 49.955
2019-11-01 | 11:23 | 49.954
2019-11-01 | 11:23 | 49.954
2019-11-01 | 11:23 | 49.953
2019-11-01 | 11:23 | 49.952
2019-11-01 | 11:23 | 49.95
2019-11-01 | 11:23 | 49.948
2019-11-01 | 11:23 | 49.946
2019-11-01 | 11:23 | 49.945
2019-11-01 | 11:23 | 49.945
2019-11-01 | 11:23 | 49.946
2019-11-01 | 11:23 | 49.947
2019-11-01 | 11:23 | 49.95
2019-11-01 | 11:23 | 49.952
2019-11-01 | 11:23 | 49.954
2019-11-01 | 11:23 | 49.955
2019-11-01 | 11:23 | 49.954
2019-11-01 | 11:23 | 49.955
2019-11-01 | 11:23 | 49.936
2019-11-01 | 11:23 | 49.914
2019-11-01 | 11:23 | 49.898
2019-11-01 | 11:23 | 49.884
2019-11-01 | 11:23 | 49.876
2019-11-01 | 11:23 | 49.87
2019-11-01 | 11:23 | 49.866
2019-11-01 | 11:23 | 49.864
2019-11-01 | 11:23 | 49.862
2019-11-01 | 11:23 | 49.861
2019-11-01 | 11:23 | 49.862
2019-11-01 | 11:23 | 49.863
2019-11-01 | 11:23 | 49.864
2019-11-01 | 11:23 | 49.865
2019-11-01 | 11:23 | 49.865
2019-11-01 | 11:23 | 49.867
2019-11-01 | 11:24 | 49.868
2019-11-01 | 11:24 | 49.87
2019-11-01 | 11:24 | 49.872
2019-11-01 | 11:24 | 49.876
2019-11-01 | 11:24 | 49.877
2019-11-01 | 11:24 | 49.879
2019-11-01 | 11:24 | 49.879
2019-11-01 | 11:24 | 49.88
2019-11-01 | 11:24 | 49.88
2019-11-01 | 11:24 | 49.88
2019-11-01 | 11:24 | 49.88
2019-11-01 | 11:24 | 49.879
2019-11-01 | 11:24 | 49.879
2019-11-01 | 11:24 | 49.879
2019-11-01 | 11:24 | 49.879
2019-11-01 | 11:24 | 49.878
2019-11-01 | 11:24 | 49.877
2019-11-01 | 11:24 | 49.876
2019-11-01 | 11:24 | 49.875
2019-11-01 | 11:24 | 49.875
2019-11-01 | 11:24 | 49.874
2019-11-01 | 11:24 | 49.873
2019-11-01 | 11:24 | 49.871
2019-11-01 | 11:24 | 49.87
2019-11-01 | 11:24 | 49.867
2019-11-01 | 11:24 | 49.863
2019-11-01 | 11:24 | 49.86
2019-11-01 | 11:24 | 49.857
2019-11-01 | 11:24 | 49.854
2019-11-01 | 11:24 | 49.853
2019-11-01 | 11:24 | 49.852
2019-11-01 | 11:24 | 49.852
2019-11-01 | 11:24 | 49.852
2019-11-01 | 11:24 | 49.853
2019-11-01 | 11:24 | 49.855
2019-11-01 | 11:24 | 49.856
2019-11-01 | 11:24 | 49.858
2019-11-01 | 11:24 | 49.858
2019-11-01 | 11:24 | 49.857
2019-11-01 | 11:24 | 49.857
2019-11-01 | 11:24 | 49.856
2019-11-01 | 11:24 | 49.855
2019-11-01 | 11:24 | 49.854
2019-11-01 | 11:24 | 49.855
2019-11-01 | 11:24 | 49.853
2019-11-01 | 11:24 | 49.852
2019-11-01 | 11:24 | 49.85
2019-11-01 | 11:24 | 49.849
2019-11-01 | 11:24 | 49.848
2019-11-01 | 11:24 | 49.848
2019-11-01 | 11:24 | 49.848
2019-11-01 | 11:24 | 49.846
2019-11-01 | 11:24 | 49.845
2019-11-01 | 11:24 | 49.845
2019-11-01 | 11:24 | 49.846
2019-11-01 | 11:24 | 49.846
2019-11-01 | 11:24 | 49.845
2019-11-01 | 11:24 | 49.843
2019-11-01 | 11:24 | 49.844
2019-11-01 | 11:24 | 49.843
2019-11-01 | 11:24 | 49.843
2019-11-01 | 11:25 | 49.843
2019-11-01 | 11:25 | 49.844
2019-11-01 | 11:25 | 49.847
2019-11-01 | 11:25 | 49.85
2019-11-01 | 11:25 | 49.852
2019-11-01 | 11:25 | 49.852
2019-11-01 | 11:25 | 49.852
2019-11-01 | 11:25 | 49.853
2019-11-01 | 11:25 | 49.855
2019-11-01 | 11:25 | 49.857
2019-11-01 | 11:25 | 49.86
2019-11-01 | 11:25 | 49.863
2019-11-01 | 11:25 | 49.865
2019-11-01 | 11:25 | 49.867
2019-11-01 | 11:25 | 49.869
2019-11-01 | 11:25 | 49.87
2019-11-01 | 11:25 | 49.871
2019-11-01 | 11:25 | 49.871
2019-11-01 | 11:25 | 49.872
2019-11-01 | 11:25 | 49.87
2019-11-01 | 11:25 | 49.869
2019-11-01 | 11:25 | 49.868
2019-11-01 | 11:25 | 49.866
2019-11-01 | 11:25 | 49.865
2019-11-01 | 11:25 | 49.864
2019-11-01 | 11:25 | 49.864
2019-11-01 | 11:25 | 49.861
2019-11-01 | 11:25 | 49.86
2019-11-01 | 11:25 | 49.859
2019-11-01 | 11:25 | 49.857
2019-11-01 | 11:25 | 49.856
2019-11-01 | 11:25 | 49.856
2019-11-01 | 11:25 | 49.855
2019-11-01 | 11:25 | 49.855
2019-11-01 | 11:25 | 49.855
2019-11-01 | 11:25 | 49.855
2019-11-01 | 11:25 | 49.855
2019-11-01 | 11:25 | 49.857
2019-11-01 | 11:25 | 49.858
2019-11-01 | 11:25 | 49.858
2019-11-01 | 11:25 | 49.859
2019-11-01 | 11:25 | 49.858
2019-11-01 | 11:25 | 49.858
2019-11-01 | 11:25 | 49.857
2019-11-01 | 11:25 | 49.857
2019-11-01 | 11:25 | 49.857
2019-11-01 | 11:25 | 49.858
2019-11-01 | 11:25 | 49.857
2019-11-01 | 11:25 | 49.858
2019-11-01 | 11:25 | 49.859
2019-11-01 | 11:25 | 49.86
2019-11-01 | 11:25 | 49.86
2019-11-01 | 11:25 | 49.861
2019-11-01 | 11:25 | 49.862
2019-11-01 | 11:25 | 49.862
2019-11-01 | 11:25 | 49.863
2019-11-01 | 11:25 | 49.864
2019-11-01 | 11:25 | 49.867
2019-11-01 | 11:25 | 49.869
2019-11-01 | 11:26 | 49.871
2019-11-01 | 11:26 | 49.872
2019-11-01 | 11:26 | 49.872
2019-11-01 | 11:26 | 49.875
2019-11-01 | 11:26 | 49.875
2019-11-01 | 11:26 | 49.875
2019-11-01 | 11:26 | 49.872
2019-11-01 | 11:26 | 49.869
2019-11-01 | 11:26 | 49.864
2019-11-01 | 11:26 | 49.861
2019-11-01 | 11:26 | 49.86
2019-11-01 | 11:26 | 49.86
2019-11-01 | 11:26 | 49.858
2019-11-01 | 11:26 | 49.857
2019-11-01 | 11:26 | 49.857
2019-11-01 | 11:26 | 49.856
2019-11-01 | 11:26 | 49.856
2019-11-01 | 11:26 | 49.856
2019-11-01 | 11:26 | 49.857
2019-11-01 | 11:26 | 49.855
2019-11-01 | 11:26 | 49.854
2019-11-01 | 11:26 | 49.853
2019-11-01 | 11:26 | 49.853
2019-11-01 | 11:26 | 49.854
2019-11-01 | 11:26 | 49.858
2019-11-01 | 11:26 | 49.863
2019-11-01 | 11:26 | 49.866
2019-11-01 | 11:26 | 49.868
2019-11-01 | 11:26 | 49.871
2019-11-01 | 11:26 | 49.872
2019-11-01 | 11:26 | 49.873
2019-11-01 | 11:26 | 49.873
2019-11-01 | 11:26 | 49.873
2019-11-01 | 11:26 | 49.873
2019-11-01 | 11:26 | 49.872
2019-11-01 | 11:26 | 49.873
2019-11-01 | 11:26 | 49.87
2019-11-01 | 11:26 | 49.87
2019-11-01 | 11:26 | 49.868
2019-11-01 | 11:26 | 49.867
2019-11-01 | 11:26 | 49.865
2019-11-01 | 11:26 | 49.863
2019-11-01 | 11:26 | 49.862
2019-11-01 | 11:26 | 49.86
2019-11-01 | 11:26 | 49.861
2019-11-01 | 11:26 | 49.862
2019-11-01 | 11:26 | 49.861
2019-11-01 | 11:26 | 49.86
2019-11-01 | 11:26 | 49.859
2019-11-01 | 11:26 | 49.859
2019-11-01 | 11:26 | 49.858
2019-11-01 | 11:26 | 49.856
2019-11-01 | 11:26 | 49.853
2019-11-01 | 11:26 | 49.852
2019-11-01 | 11:26 | 49.851
2019-11-01 | 11:26 | 49.852
2019-11-01 | 11:26 | 49.853
2019-11-01 | 11:26 | 49.853
2019-11-01 | 11:26 | 49.856
2019-11-01 | 11:26 | 49.858
2019-11-01 | 11:26 | 49.861
2019-11-01 | 11:27 | 49.865
2019-11-01 | 11:27 | 49.868
2019-11-01 | 11:27 | 49.872
2019-11-01 | 11:27 | 49.874
2019-11-01 | 11:27 | 49.875
2019-11-01 | 11:27 | 49.874
2019-11-01 | 11:27 | 49.872
2019-11-01 | 11:27 | 49.87
2019-11-01 | 11:27 | 49.868
2019-11-01 | 11:27 | 49.866
2019-11-01 | 11:27 | 49.866
2019-11-01 | 11:27 | 49.867
2019-11-01 | 11:27 | 49.868
2019-11-01 | 11:27 | 49.868
2019-11-01 | 11:27 | 49.867
2019-11-01 | 11:27 | 49.864
2019-11-01 | 11:27 | 49.861
2019-11-01 | 11:27 | 49.859
2019-11-01 | 11:27 | 49.856
2019-11-01 | 11:27 | 49.852
2019-11-01 | 11:27 | 49.847
2019-11-01 | 11:27 | 49.844
2019-11-01 | 11:27 | 49.84
2019-11-01 | 11:27 | 49.837
2019-11-01 | 11:27 | 49.836
2019-11-01 | 11:27 | 49.835
2019-11-01 | 11:27 | 49.836
2019-11-01 | 11:27 | 49.837
2019-11-01 | 11:27 | 49.839
2019-11-01 | 11:27 | 49.84
2019-11-01 | 11:27 | 49.841
2019-11-01 | 11:27 | 49.843
2019-11-01 | 11:27 | 49.845
2019-11-01 | 11:27 | 49.849
2019-11-01 | 11:27 | 49.85
2019-11-01 | 11:27 | 49.854
2019-11-01 | 11:27 | 49.858
2019-11-01 | 11:27 | 49.86
2019-11-01 | 11:27 | 49.862
2019-11-01 | 11:27 | 49.864
2019-11-01 | 11:27 | 49.864
2019-11-01 | 11:27 | 49.864
2019-11-01 | 11:27 | 49.864
2019-11-01 | 11:27 | 49.865
2019-11-01 | 11:27 | 49.866
2019-11-01 | 11:27 | 49.869
2019-11-01 | 11:27 | 49.872
2019-11-01 | 11:27 | 49.876
2019-11-01 | 11:27 | 49.879
2019-11-01 | 11:27 | 49.881
2019-11-01 | 11:27 | 49.883
2019-11-01 | 11:27 | 49.884
2019-11-01 | 11:27 | 49.884
2019-11-01 | 11:27 | 49.883
2019-11-01 | 11:27 | 49.883
2019-11-01 | 11:27 | 49.883
2019-11-01 | 11:27 | 49.884
2019-11-01 | 11:27 | 49.885
2019-11-01 | 11:27 | 49.885
2019-11-01 | 11:28 | 49.885
2019-11-01 | 11:28 | 49.884
2019-11-01 | 11:28 | 49.885
2019-11-01 | 11:28 | 49.885
2019-11-01 | 11:28 | 49.883
2019-11-01 | 11:28 | 49.882
2019-11-01 | 11:28 | 49.88
2019-11-01 | 11:28 | 49.88
2019-11-01 | 11:28 | 49.879
2019-11-01 | 11:28 | 49.878
2019-11-01 | 11:28 | 49.88
2019-11-01 | 11:28 | 49.882
2019-11-01 | 11:28 | 49.883
2019-11-01 | 11:28 | 49.886
2019-11-01 | 11:28 | 49.89
2019-11-01 | 11:28 | 49.893
2019-11-01 | 11:28 | 49.896
2019-11-01 | 11:28 | 49.9
2019-11-01 | 11:28 | 49.901
2019-11-01 | 11:28 | 49.901
2019-11-01 | 11:28 | 49.902
2019-11-01 | 11:28 | 49.903
2019-11-01 | 11:28 | 49.904
2019-11-01 | 11:28 | 49.905
2019-11-01 | 11:28 | 49.905
2019-11-01 | 11:28 | 49.903
2019-11-01 | 11:28 | 49.904
2019-11-01 | 11:28 | 49.906
2019-11-01 | 11:28 | 49.909
2019-11-01 | 11:28 | 49.912
2019-11-01 | 11:28 | 49.911
2019-11-01 | 11:28 | 49.911
2019-11-01 | 11:28 | 49.908
2019-11-01 | 11:28 | 49.907
2019-11-01 | 11:28 | 49.905
2019-11-01 | 11:28 | 49.906
2019-11-01 | 11:28 | 49.905
2019-11-01 | 11:28 | 49.905
2019-11-01 | 11:28 | 49.905
2019-11-01 | 11:28 | 49.904
2019-11-01 | 11:28 | 49.904
2019-11-01 | 11:28 | 49.905
2019-11-01 | 11:28 | 49.905
2019-11-01 | 11:28 | 49.907
2019-11-01 | 11:28 | 49.909
2019-11-01 | 11:28 | 49.909
2019-11-01 | 11:28 | 49.91
2019-11-01 | 11:28 | 49.912
2019-11-01 | 11:28 | 49.915
2019-11-01 | 11:28 | 49.919
2019-11-01 | 11:28 | 49.923
2019-11-01 | 11:28 | 49.928
2019-11-01 | 11:28 | 49.931
2019-11-01 | 11:28 | 49.934
2019-11-01 | 11:28 | 49.936
2019-11-01 | 11:28 | 49.937
2019-11-01 | 11:28 | 49.937
2019-11-01 | 11:28 | 49.936
2019-11-01 | 11:28 | 49.936
2019-11-01 | 11:28 | 49.938
2019-11-01 | 11:28 | 49.944
2019-11-01 | 11:29 | 49.949
2019-11-01 | 11:29 | 49.953
2019-11-01 | 11:29 | 49.957
2019-11-01 | 11:29 | 49.958
2019-11-01 | 11:29 | 49.958
2019-11-01 | 11:29 | 49.958
2019-11-01 | 11:29 | 49.957
2019-11-01 | 11:29 | 49.955
2019-11-01 | 11:29 | 49.952
2019-11-01 | 11:29 | 49.947
2019-11-01 | 11:29 | 49.944
2019-11-01 | 11:29 | 49.941
2019-11-01 | 11:29 | 49.94
2019-11-01 | 11:29 | 49.939
2019-11-01 | 11:29 | 49.941
2019-11-01 | 11:29 | 49.944
2019-11-01 | 11:29 | 49.945
2019-11-01 | 11:29 | 49.947
2019-11-01 | 11:29 | 49.951
2019-11-01 | 11:29 | 49.954
2019-11-01 | 11:29 | 49.956
2019-11-01 | 11:29 | 49.958
2019-11-01 | 11:29 | 49.959
2019-11-01 | 11:29 | 49.959
2019-11-01 | 11:29 | 49.96
2019-11-01 | 11:29 | 49.961
2019-11-01 | 11:29 | 49.96
2019-11-01 | 11:29 | 49.959
2019-11-01 | 11:29 | 49.956
2019-11-01 | 11:29 | 49.955
2019-11-01 | 11:29 | 49.954
2019-11-01 | 11:29 | 49.954
2019-11-01 | 11:29 | 49.953
2019-11-01 | 11:29 | 49.955
2019-11-01 | 11:29 | 49.955
2019-11-01 | 11:29 | 49.955
2019-11-01 | 11:29 | 49.955
2019-11-01 | 11:29 | 49.954
2019-11-01 | 11:29 | 49.951
2019-11-01 | 11:29 | 49.95
2019-11-01 | 11:29 | 49.949
2019-11-01 | 11:29 | 49.949
2019-11-01 | 11:29 | 49.949
2019-11-01 | 11:29 | 49.95
2019-11-01 | 11:29 | 49.952
2019-11-01 | 11:29 | 49.954
2019-11-01 | 11:29 | 49.956
2019-11-01 | 11:29 | 49.959
2019-11-01 | 11:29 | 49.962
2019-11-01 | 11:29 | 49.967
2019-11-01 | 11:29 | 49.97
2019-11-01 | 11:29 | 49.973
2019-11-01 | 11:29 | 49.976
2019-11-01 | 11:29 | 49.979
2019-11-01 | 11:29 | 49.982
2019-11-01 | 11:29 | 49.985
2019-11-01 | 11:29 | 49.986
2019-11-01 | 11:29 | 49.987
2019-11-01 | 11:29 | 49.986
2019-11-01 | 11:30 | 49.986
2019-11-01 | 11:30 | 49.986
2019-11-01 | 11:30 | 49.987
2019-11-01 | 11:30 | 49.987
2019-11-01 | 11:30 | 49.99
2019-11-01 | 11:30 | 49.993
2019-11-01 | 11:30 | 49.998
2019-11-01 | 11:30 | 50.003
2019-11-01 | 11:30 | 50.007
2019-11-01 | 11:30 | 50.011
2019-11-01 | 11:30 | 50.014
2019-11-01 | 11:30 | 50.016
2019-11-01 | 11:30 | 50.017
2019-11-01 | 11:30 | 50.017
2019-11-01 | 11:30 | 50.017
2019-11-01 | 11:30 | 50.017
2019-11-01 | 11:30 | 50.017
2019-11-01 | 11:30 | 50.016
2019-11-01 | 11:30 | 50.012
2019-11-01 | 11:30 | 50.008
2019-11-01 | 11:30 | 50
2019-11-01 | 11:30 | 49.993
2019-11-01 | 11:30 | 49.982
2019-11-01 | 11:30 | 49.97
2019-11-01 | 11:30 | 49.96
2019-11-01 | 11:30 | 49.958
2019-11-01 | 11:30 | 49.957
2019-11-01 | 11:30 | 49.961
2019-11-01 | 11:30 | 49.963
2019-11-01 | 11:30 | 49.964

## Event 20191101-3
In UTC
Date | Time | Freq
2019-11-01 | 18:50 | 49.938
2019-11-01 | 18:50 | 49.937
2019-11-01 | 18:50 | 49.935
2019-11-01 | 18:50 | 49.933
2019-11-01 | 18:50 | 49.933
2019-11-01 | 18:50 | 49.934
2019-11-01 | 18:50 | 49.936
2019-11-01 | 18:50 | 49.937
2019-11-01 | 18:50 | 49.939
2019-11-01 | 18:50 | 49.94
2019-11-01 | 18:50 | 49.938
2019-11-01 | 18:50 | 49.936
2019-11-01 | 18:50 | 49.934
2019-11-01 | 18:50 | 49.932
2019-11-01 | 18:50 | 49.932
2019-11-01 | 18:50 | 49.932
2019-11-01 | 18:50 | 49.931
2019-11-01 | 18:50 | 49.931
2019-11-01 | 18:50 | 49.931
2019-11-01 | 18:50 | 49.931
2019-11-01 | 18:50 | 49.932
2019-11-01 | 18:50 | 49.931
2019-11-01 | 18:50 | 49.931
2019-11-01 | 18:50 | 49.932
2019-11-01 | 18:50 | 49.932
2019-11-01 | 18:50 | 49.935
2019-11-01 | 18:50 | 49.939
2019-11-01 | 18:50 | 49.94
2019-11-01 | 18:50 | 49.944
2019-11-01 | 18:50 | 49.947
2019-11-01 | 18:50 | 49.949
2019-11-01 | 18:51 | 49.951
2019-11-01 | 18:51 | 49.953
2019-11-01 | 18:51 | 49.955
2019-11-01 | 18:51 | 49.954
2019-11-01 | 18:51 | 49.952
2019-11-01 | 18:51 | 49.95
2019-11-01 | 18:51 | 49.949
2019-11-01 | 18:51 | 49.951
2019-11-01 | 18:51 | 49.955
2019-11-01 | 18:51 | 49.958
2019-11-01 | 18:51 | 49.961
2019-11-01 | 18:51 | 49.963
2019-11-01 | 18:51 | 49.965
2019-11-01 | 18:51 | 49.965
2019-11-01 | 18:51 | 49.964
2019-11-01 | 18:51 | 49.963
2019-11-01 | 18:51 | 49.961
2019-11-01 | 18:51 | 49.959
2019-11-01 | 18:51 | 49.959
2019-11-01 | 18:51 | 49.961
2019-11-01 | 18:51 | 49.961
2019-11-01 | 18:51 | 49.959
2019-11-01 | 18:51 | 49.957
2019-11-01 | 18:51 | 49.955
2019-11-01 | 18:51 | 49.954
2019-11-01 | 18:51 | 49.954
2019-11-01 | 18:51 | 49.952
2019-11-01 | 18:51 | 49.951
2019-11-01 | 18:51 | 49.949
2019-11-01 | 18:51 | 49.949
2019-11-01 | 18:51 | 49.952
2019-11-01 | 18:51 | 49.954
2019-11-01 | 18:51 | 49.957
2019-11-01 | 18:51 | 49.96
2019-11-01 | 18:51 | 49.963
2019-11-01 | 18:51 | 49.967
2019-11-01 | 18:51 | 49.969
2019-11-01 | 18:51 | 49.972
2019-11-01 | 18:51 | 49.975
2019-11-01 | 18:51 | 49.977
2019-11-01 | 18:51 | 49.977
2019-11-01 | 18:51 | 49.977
2019-11-01 | 18:51 | 49.977
2019-11-01 | 18:51 | 49.977
2019-11-01 | 18:51 | 49.977
2019-11-01 | 18:51 | 49.977
2019-11-01 | 18:51 | 49.976
2019-11-01 | 18:51 | 49.975
2019-11-01 | 18:51 | 49.972
2019-11-01 | 18:51 | 49.974
2019-11-01 | 18:51 | 49.974
2019-11-01 | 18:51 | 49.975
2019-11-01 | 18:51 | 49.971
2019-11-01 | 18:51 | 49.97
2019-11-01 | 18:51 | 49.969
2019-11-01 | 18:51 | 49.967
2019-11-01 | 18:51 | 49.966
2019-11-01 | 18:51 | 49.966
2019-11-01 | 18:51 | 49.968
2019-11-01 | 18:52 | 49.971
2019-11-01 | 18:52 | 49.972
2019-11-01 | 18:52 | 49.974
2019-11-01 | 18:52 | 49.974
2019-11-01 | 18:52 | 49.974
2019-11-01 | 18:52 | 49.978
2019-11-01 | 18:52 | 49.979
2019-11-01 | 18:52 | 49.979
2019-11-01 | 18:52 | 49.974
2019-11-01 | 18:52 | 49.968
2019-11-01 | 18:52 | 49.961
2019-11-01 | 18:52 | 49.94
2019-11-01 | 18:52 | 49.911
2019-11-01 | 18:52 | 49.887
2019-11-01 | 18:52 | 49.869
2019-11-01 | 18:52 | 49.863
2019-11-01 | 18:52 | 49.865
2019-11-01 | 18:52 | 49.874
2019-11-01 | 18:52 | 49.885
2019-11-01 | 18:52 | 49.894
2019-11-01 | 18:52 | 49.9
2019-11-01 | 18:52 | 49.904
2019-11-01 | 18:52 | 49.906
2019-11-01 | 18:52 | 49.908
2019-11-01 | 18:52 | 49.911
2019-11-01 | 18:52 | 49.913
2019-11-01 | 18:52 | 49.917
2019-11-01 | 18:52 | 49.92
2019-11-01 | 18:52 | 49.922
2019-11-01 | 18:52 | 49.921
2019-11-01 | 18:52 | 49.92
2019-11-01 | 18:52 | 49.919
2019-11-01 | 18:52 | 49.917
2019-11-01 | 18:52 | 49.916
2019-11-01 | 18:52 | 49.915
2019-11-01 | 18:52 | 49.914
2019-11-01 | 18:52 | 49.913
2019-11-01 | 18:52 | 49.911
2019-11-01 | 18:52 | 49.908
2019-11-01 | 18:52 | 49.905
2019-11-01 | 18:52 | 49.903
2019-11-01 | 18:52 | 49.902
2019-11-01 | 18:52 | 49.899
2019-11-01 | 18:52 | 49.897
2019-11-01 | 18:52 | 49.895
2019-11-01 | 18:52 | 49.894
2019-11-01 | 18:52 | 49.894
2019-11-01 | 18:52 | 49.894
2019-11-01 | 18:52 | 49.894
2019-11-01 | 18:52 | 49.893
2019-11-01 | 18:52 | 49.893
2019-11-01 | 18:52 | 49.892
2019-11-01 | 18:52 | 49.892
2019-11-01 | 18:52 | 49.893
2019-11-01 | 18:52 | 49.894
2019-11-01 | 18:52 | 49.897
2019-11-01 | 18:52 | 49.9
2019-11-01 | 18:52 | 49.902
2019-11-01 | 18:52 | 49.903
2019-11-01 | 18:52 | 49.903
2019-11-01 | 18:52 | 49.901
2019-11-01 | 18:53 | 49.899
2019-11-01 | 18:53 | 49.896
2019-11-01 | 18:53 | 49.891
2019-11-01 | 18:53 | 49.888
2019-11-01 | 18:53 | 49.886
2019-11-01 | 18:53 | 49.884
2019-11-01 | 18:53 | 49.882
2019-11-01 | 18:53 | 49.882
2019-11-01 | 18:53 | 49.88
2019-11-01 | 18:53 | 49.878
2019-11-01 | 18:53 | 49.877
2019-11-01 | 18:53 | 49.875
2019-11-01 | 18:53 | 49.875
2019-11-01 | 18:53 | 49.872
2019-11-01 | 18:53 | 49.87
2019-11-01 | 18:53 | 49.87
2019-11-01 | 18:53 | 49.871
2019-11-01 | 18:53 | 49.871
2019-11-01 | 18:53 | 49.87
2019-11-01 | 18:53 | 49.871
2019-11-01 | 18:53 | 49.871
2019-11-01 | 18:53 | 49.871
2019-11-01 | 18:53 | 49.871
2019-11-01 | 18:53 | 49.871
2019-11-01 | 18:53 | 49.873
2019-11-01 | 18:53 | 49.872
2019-11-01 | 18:53 | 49.871
2019-11-01 | 18:53 | 49.869
2019-11-01 | 18:53 | 49.865
2019-11-01 | 18:53 | 49.863
2019-11-01 | 18:53 | 49.861
2019-11-01 | 18:53 | 49.863
2019-11-01 | 18:53 | 49.865
2019-11-01 | 18:53 | 49.867
2019-11-01 | 18:53 | 49.871
2019-11-01 | 18:53 | 49.874
2019-11-01 | 18:53 | 49.876
2019-11-01 | 18:53 | 49.879
2019-11-01 | 18:53 | 49.882
2019-11-01 | 18:53 | 49.881
2019-11-01 | 18:53 | 49.882
2019-11-01 | 18:53 | 49.881
2019-11-01 | 18:53 | 49.882
2019-11-01 | 18:53 | 49.881
2019-11-01 | 18:53 | 49.881
2019-11-01 | 18:53 | 49.88
2019-11-01 | 18:53 | 49.88
2019-11-01 | 18:53 | 49.878
2019-11-01 | 18:53 | 49.877
2019-11-01 | 18:53 | 49.874
2019-11-01 | 18:53 | 49.874
2019-11-01 | 18:53 | 49.873
2019-11-01 | 18:53 | 49.872
2019-11-01 | 18:53 | 49.87
2019-11-01 | 18:53 | 49.869
2019-11-01 | 18:53 | 49.868
2019-11-01 | 18:53 | 49.866
2019-11-01 | 18:53 | 49.862
2019-11-01 | 18:53 | 49.861
2019-11-01 | 18:54 | 49.86
2019-11-01 | 18:54 | 49.859
2019-11-01 | 18:54 | 49.855
2019-11-01 | 18:54 | 49.855
2019-11-01 | 18:54 | 49.856
2019-11-01 | 18:54 | 49.858
2019-11-01 | 18:54 | 49.86
2019-11-01 | 18:54 | 49.863
2019-11-01 | 18:54 | 49.865
2019-11-01 | 18:54 | 49.867
2019-11-01 | 18:54 | 49.87
2019-11-01 | 18:54 | 49.873
2019-11-01 | 18:54 | 49.874
2019-11-01 | 18:54 | 49.877
2019-11-01 | 18:54 | 49.877
2019-11-01 | 18:54 | 49.877
2019-11-01 | 18:54 | 49.877
2019-11-01 | 18:54 | 49.875
2019-11-01 | 18:54 | 49.873
2019-11-01 | 18:54 | 49.87
2019-11-01 | 18:54 | 49.868
2019-11-01 | 18:54 | 49.867
2019-11-01 | 18:54 | 49.863
2019-11-01 | 18:54 | 49.86
2019-11-01 | 18:54 | 49.855
2019-11-01 | 18:54 | 49.855
2019-11-01 | 18:54 | 49.855
2019-11-01 | 18:54 | 49.855
2019-11-01 | 18:54 | 49.854
2019-11-01 | 18:54 | 49.853
2019-11-01 | 18:54 | 49.852
2019-11-01 | 18:54 | 49.851
2019-11-01 | 18:54 | 49.853
2019-11-01 | 18:54 | 49.854
2019-11-01 | 18:54 | 49.856
2019-11-01 | 18:54 | 49.856
2019-11-01 | 18:54 | 49.856
2019-11-01 | 18:54 | 49.857
2019-11-01 | 18:54 | 49.858
2019-11-01 | 18:54 | 49.859
2019-11-01 | 18:54 | 49.861
2019-11-01 | 18:54 | 49.863
2019-11-01 | 18:54 | 49.865
2019-11-01 | 18:54 | 49.866
2019-11-01 | 18:54 | 49.866
2019-11-01 | 18:54 | 49.867
2019-11-01 | 18:54 | 49.865
2019-11-01 | 18:54 | 49.864
2019-11-01 | 18:54 | 49.865
2019-11-01 | 18:54 | 49.867
2019-11-01 | 18:54 | 49.868
2019-11-01 | 18:54 | 49.87
2019-11-01 | 18:54 | 49.873
2019-11-01 | 18:54 | 49.874
2019-11-01 | 18:54 | 49.874
2019-11-01 | 18:54 | 49.873
2019-11-01 | 18:54 | 49.873
2019-11-01 | 18:54 | 49.872
2019-11-01 | 18:54 | 49.871
2019-11-01 | 18:54 | 49.871
2019-11-01 | 18:54 | 49.871
2019-11-01 | 18:55 | 49.87
2019-11-01 | 18:55 | 49.87
2019-11-01 | 18:55 | 49.87
2019-11-01 | 18:55 | 49.871
2019-11-01 | 18:55 | 49.871
2019-11-01 | 18:55 | 49.871
2019-11-01 | 18:55 | 49.871
2019-11-01 | 18:55 | 49.871
2019-11-01 | 18:55 | 49.871
2019-11-01 | 18:55 | 49.872
2019-11-01 | 18:55 | 49.872
2019-11-01 | 18:55 | 49.873
2019-11-01 | 18:55 | 49.875
2019-11-01 | 18:55 | 49.878
2019-11-01 | 18:55 | 49.88
2019-11-01 | 18:55 | 49.881
2019-11-01 | 18:55 | 49.881
2019-11-01 | 18:55 | 49.882
2019-11-01 | 18:55 | 49.883
2019-11-01 | 18:55 | 49.882
2019-11-01 | 18:55 | 49.882
2019-11-01 | 18:55 | 49.881
2019-11-01 | 18:55 | 49.882
2019-11-01 | 18:55 | 49.883
2019-11-01 | 18:55 | 49.885
2019-11-01 | 18:55 | 49.885
2019-11-01 | 18:55 | 49.886
2019-11-01 | 18:55 | 49.885
2019-11-01 | 18:55 | 49.883
2019-11-01 | 18:55 | 49.882
2019-11-01 | 18:55 | 49.88
2019-11-01 | 18:55 | 49.877
2019-11-01 | 18:55 | 49.875
2019-11-01 | 18:55 | 49.874
2019-11-01 | 18:55 | 49.873
2019-11-01 | 18:55 | 49.871
2019-11-01 | 18:55 | 49.87
2019-11-01 | 18:55 | 49.869
2019-11-01 | 18:55 | 49.867
2019-11-01 | 18:55 | 49.864
2019-11-01 | 18:55 | 49.862
2019-11-01 | 18:55 | 49.862
2019-11-01 | 18:55 | 49.863
2019-11-01 | 18:55 | 49.863
2019-11-01 | 18:55 | 49.861
2019-11-01 | 18:55 | 49.86
2019-11-01 | 18:55 | 49.861
2019-11-01 | 18:55 | 49.862
2019-11-01 | 18:55 | 49.863
2019-11-01 | 18:55 | 49.865
2019-11-01 | 18:55 | 49.868
2019-11-01 | 18:55 | 49.869
2019-11-01 | 18:55 | 49.873
2019-11-01 | 18:55 | 49.875
2019-11-01 | 18:55 | 49.878
2019-11-01 | 18:55 | 49.881
2019-11-01 | 18:55 | 49.884
2019-11-01 | 18:55 | 49.888
2019-11-01 | 18:55 | 49.893
2019-11-01 | 18:56 | 49.898
2019-11-01 | 18:56 | 49.902
2019-11-01 | 18:56 | 49.906
2019-11-01 | 18:56 | 49.909
2019-11-01 | 18:56 | 49.911
2019-11-01 | 18:56 | 49.914
2019-11-01 | 18:56 | 49.916
2019-11-01 | 18:56 | 49.918
2019-11-01 | 18:56 | 49.92
2019-11-01 | 18:56 | 49.919
2019-11-01 | 18:56 | 49.919
2019-11-01 | 18:56 | 49.92
2019-11-01 | 18:56 | 49.922
2019-11-01 | 18:56 | 49.927
2019-11-01 | 18:56 | 49.932
2019-11-01 | 18:56 | 49.936
2019-11-01 | 18:56 | 49.94
2019-11-01 | 18:56 | 49.941
2019-11-01 | 18:56 | 49.942
2019-11-01 | 18:56 | 49.942
2019-11-01 | 18:56 | 49.941
2019-11-01 | 18:56 | 49.941
2019-11-01 | 18:56 | 49.94
2019-11-01 | 18:56 | 49.941
2019-11-01 | 18:56 | 49.941
2019-11-01 | 18:56 | 49.944
2019-11-01 | 18:56 | 49.946
2019-11-01 | 18:56 | 49.949
2019-11-01 | 18:56 | 49.951
2019-11-01 | 18:56 | 49.952
2019-11-01 | 18:56 | 49.952
2019-11-01 | 18:56 | 49.951
2019-11-01 | 18:56 | 49.952
2019-11-01 | 18:56 | 49.951
2019-11-01 | 18:56 | 49.949
2019-11-01 | 18:56 | 49.946
2019-11-01 | 18:56 | 49.942
2019-11-01 | 18:56 | 49.939
2019-11-01 | 18:56 | 49.937
2019-11-01 | 18:56 | 49.935
2019-11-01 | 18:56 | 49.934
2019-11-01 | 18:56 | 49.936
2019-11-01 | 18:56 | 49.938
2019-11-01 | 18:56 | 49.938
2019-11-01 | 18:56 | 49.937
2019-11-01 | 18:56 | 49.936
2019-11-01 | 18:56 | 49.934
2019-11-01 | 18:56 | 49.933
2019-11-01 | 18:56 | 49.93
2019-11-01 | 18:56 | 49.926
2019-11-01 | 18:56 | 49.925
2019-11-01 | 18:56 | 49.925
2019-11-01 | 18:56 | 49.926
2019-11-01 | 18:56 | 49.928
2019-11-01 | 18:56 | 49.929
2019-11-01 | 18:56 | 49.93
2019-11-01 | 18:56 | 49.932
2019-11-01 | 18:56 | 49.932
2019-11-01 | 18:56 | 49.935
2019-11-01 | 18:56 | 49.936
2019-11-01 | 18:56 | 49.937
2019-11-01 | 18:57 | 49.939
2019-11-01 | 18:57 | 49.942
2019-11-01 | 18:57 | 49.943
2019-11-01 | 18:57 | 49.945
2019-11-01 | 18:57 | 49.945
2019-11-01 | 18:57 | 49.944
2019-11-01 | 18:57 | 49.944
2019-11-01 | 18:57 | 49.945
2019-11-01 | 18:57 | 49.948
2019-11-01 | 18:57 | 49.95
2019-11-01 | 18:57 | 49.952
2019-11-01 | 18:57 | 49.953
2019-11-01 | 18:57 | 49.954
2019-11-01 | 18:57 | 49.955
2019-11-01 | 18:57 | 49.953
2019-11-01 | 18:57 | 49.951
2019-11-01 | 18:57 | 49.95
2019-11-01 | 18:57 | 49.949
2019-11-01 | 18:57 | 49.948
2019-11-01 | 18:57 | 49.947
2019-11-01 | 18:57 | 49.946
2019-11-01 | 18:57 | 49.945
2019-11-01 | 18:57 | 49.945
2019-11-01 | 18:57 | 49.946
2019-11-01 | 18:57 | 49.945
2019-11-01 | 18:57 | 49.946
2019-11-01 | 18:57 | 49.95
2019-11-01 | 18:57 | 49.955
2019-11-01 | 18:57 | 49.96
2019-11-01 | 18:57 | 49.964
2019-11-01 | 18:57 | 49.968
2019-11-01 | 18:57 | 49.971
2019-11-01 | 18:57 | 49.973
2019-11-01 | 18:57 | 49.973
2019-11-01 | 18:57 | 49.97
2019-11-01 | 18:57 | 49.966
2019-11-01 | 18:57 | 49.962
2019-11-01 | 18:57 | 49.958
2019-11-01 | 18:57 | 49.955
2019-11-01 | 18:57 | 49.952
2019-11-01 | 18:57 | 49.95
2019-11-01 | 18:57 | 49.947
2019-11-01 | 18:57 | 49.946
2019-11-01 | 18:57 | 49.943
2019-11-01 | 18:57 | 49.94
2019-11-01 | 18:57 | 49.936
2019-11-01 | 18:57 | 49.933
2019-11-01 | 18:57 | 49.927
2019-11-01 | 18:57 | 49.923
2019-11-01 | 18:57 | 49.92
2019-11-01 | 18:57 | 49.916
2019-11-01 | 18:57 | 49.912
2019-11-01 | 18:57 | 49.908
2019-11-01 | 18:57 | 49.905
2019-11-01 | 18:57 | 49.904
2019-11-01 | 18:57 | 49.905
2019-11-01 | 18:57 | 49.904
2019-11-01 | 18:57 | 49.904
2019-11-01 | 18:57 | 49.905
2019-11-01 | 18:57 | 49.907
2019-11-01 | 18:58 | 49.907
2019-11-01 | 18:58 | 49.91
2019-11-01 | 18:58 | 49.912
2019-11-01 | 18:58 | 49.917
2019-11-01 | 18:58 | 49.921
2019-11-01 | 18:58 | 49.923
2019-11-01 | 18:58 | 49.926
2019-11-01 | 18:58 | 49.928
2019-11-01 | 18:58 | 49.928
2019-11-01 | 18:58 | 49.93
2019-11-01 | 18:58 | 49.932
2019-11-01 | 18:58 | 49.932
2019-11-01 | 18:58 | 49.933
2019-11-01 | 18:58 | 49.933
2019-11-01 | 18:58 | 49.932
2019-11-01 | 18:58 | 49.932
2019-11-01 | 18:58 | 49.932
2019-11-01 | 18:58 | 49.931
2019-11-01 | 18:58 | 49.931
2019-11-01 | 18:58 | 49.931
2019-11-01 | 18:58 | 49.932
2019-11-01 | 18:58 | 49.93
2019-11-01 | 18:58 | 49.927
2019-11-01 | 18:58 | 49.925
2019-11-01 | 18:58 | 49.925
2019-11-01 | 18:58 | 49.923
2019-11-01 | 18:58 | 49.925
2019-11-01 | 18:58 | 49.924
2019-11-01 | 18:58 | 49.925
2019-11-01 | 18:58 | 49.926
2019-11-01 | 18:58 | 49.928
2019-11-01 | 18:58 | 49.928
2019-11-01 | 18:58 | 49.93
2019-11-01 | 18:58 | 49.932
2019-11-01 | 18:58 | 49.934
2019-11-01 | 18:58 | 49.935
2019-11-01 | 18:58 | 49.936
2019-11-01 | 18:58 | 49.936
2019-11-01 | 18:58 | 49.936
2019-11-01 | 18:58 | 49.936
2019-11-01 | 18:58 | 49.936
2019-11-01 | 18:58 | 49.937
2019-11-01 | 18:58 | 49.936
2019-11-01 | 18:58 | 49.935
2019-11-01 | 18:58 | 49.936
2019-11-01 | 18:58 | 49.936
2019-11-01 | 18:58 | 49.934
2019-11-01 | 18:58 | 49.934
2019-11-01 | 18:58 | 49.933
2019-11-01 | 18:58 | 49.932
2019-11-01 | 18:58 | 49.932
2019-11-01 | 18:58 | 49.931
2019-11-01 | 18:58 | 49.933
2019-11-01 | 18:58 | 49.936
2019-11-01 | 18:58 | 49.938
2019-11-01 | 18:58 | 49.943
2019-11-01 | 18:58 | 49.946
2019-11-01 | 18:58 | 49.95
2019-11-01 | 18:58 | 49.955
2019-11-01 | 18:58 | 49.957
2019-11-01 | 18:59 | 49.961
2019-11-01 | 18:59 | 49.962
2019-11-01 | 18:59 | 49.964
2019-11-01 | 18:59 | 49.965
2019-11-01 | 18:59 | 49.968
2019-11-01 | 18:59 | 49.968
2019-11-01 | 18:59 | 49.966
2019-11-01 | 18:59 | 49.965
2019-11-01 | 18:59 | 49.961
2019-11-01 | 18:59 | 49.957
2019-11-01 | 18:59 | 49.952
2019-11-01 | 18:59 | 49.95
2019-11-01 | 18:59 | 49.945
2019-11-01 | 18:59 | 49.941
2019-11-01 | 18:59 | 49.939
2019-11-01 | 18:59 | 49.937
2019-11-01 | 18:59 | 49.937
2019-11-01 | 18:59 | 49.937
2019-11-01 | 18:59 | 49.94
2019-11-01 | 18:59 | 49.944
2019-11-01 | 18:59 | 49.946
2019-11-01 | 18:59 | 49.949
2019-11-01 | 18:59 | 49.95
2019-11-01 | 18:59 | 49.952
2019-11-01 | 18:59 | 49.953
2019-11-01 | 18:59 | 49.956
2019-11-01 | 18:59 | 49.957
2019-11-01 | 18:59 | 49.957
2019-11-01 | 18:59 | 49.957
2019-11-01 | 18:59 | 49.955
2019-11-01 | 18:59 | 49.954
2019-11-01 | 18:59 | 49.956
2019-11-01 | 18:59 | 49.958
2019-11-01 | 18:59 | 49.963
2019-11-01 | 18:59 | 49.966
2019-11-01 | 18:59 | 49.969
2019-11-01 | 18:59 | 49.972
2019-11-01 | 18:59 | 49.974
2019-11-01 | 18:59 | 49.975
2019-11-01 | 18:59 | 49.974
2019-11-01 | 18:59 | 49.973
2019-11-01 | 18:59 | 49.973
2019-11-01 | 18:59 | 49.974
2019-11-01 | 18:59 | 49.976
2019-11-01 | 18:59 | 49.98
2019-11-01 | 18:59 | 49.98
2019-11-01 | 18:59 | 49.98
2019-11-01 | 18:59 | 49.981
2019-11-01 | 18:59 | 49.981
2019-11-01 | 18:59 | 49.981
2019-11-01 | 18:59 | 49.981
2019-11-01 | 18:59 | 49.982
2019-11-01 | 18:59 | 49.983
2019-11-01 | 18:59 | 49.987
2019-11-01 | 18:59 | 49.993
2019-11-01 | 18:59 | 49.998
2019-11-01 | 18:59 | 50.003
2019-11-01 | 18:59 | 50.008
2019-11-01 | 18:59 | 50.01
2019-11-01 | 19:00 | 50.012
2019-11-01 | 19:00 | 50.013
2019-11-01 | 19:00 | 50.015
2019-11-01 | 19:00 | 50.016
2019-11-01 | 19:00 | 50.018
2019-11-01 | 19:00 | 50.023
2019-11-01 | 19:00 | 50.03
2019-11-01 | 19:00 | 50.036
2019-11-01 | 19:00 | 50.042
2019-11-01 | 19:00 | 50.049
2019-11-01 | 19:00 | 50.056
2019-11-01 | 19:00 | 50.062
2019-11-01 | 19:00 | 50.067
2019-11-01 | 19:00 | 50.072
2019-11-01 | 19:00 | 50.077
2019-11-01 | 19:00 | 50.08
2019-11-01 | 19:00 | 50.084
2019-11-01 | 19:00 | 50.086
2019-11-01 | 19:00 | 50.084
2019-11-01 | 19:00 | 50.081
2019-11-01 | 19:00 | 50.078
2019-11-01 | 19:00 | 50.077
2019-11-01 | 19:00 | 50.076
2019-11-01 | 19:00 | 50.075
2019-11-01 | 19:00 | 50.077
2019-11-01 | 19:00 | 50.08
2019-11-01 | 19:00 | 50.081
2019-11-01 | 19:00 | 50.085
2019-11-01 | 19:00 | 50.091
2019-11-01 | 19:00 | 50.096

## Event 20191103-1
In UTC
Date | Time | Freq
2019-11-03 | 4:18 | 49.964
2019-11-03 | 4:18 | 49.964
2019-11-03 | 4:18 | 49.964
2019-11-03 | 4:18 | 49.965
2019-11-03 | 4:18 | 49.966
2019-11-03 | 4:18 | 49.967
2019-11-03 | 4:18 | 49.967
2019-11-03 | 4:18 | 49.967
2019-11-03 | 4:18 | 49.967
2019-11-03 | 4:18 | 49.968
2019-11-03 | 4:18 | 49.969
2019-11-03 | 4:18 | 49.969
2019-11-03 | 4:18 | 49.97
2019-11-03 | 4:18 | 49.972
2019-11-03 | 4:18 | 49.976
2019-11-03 | 4:18 | 49.979
2019-11-03 | 4:18 | 49.982
2019-11-03 | 4:18 | 49.986
2019-11-03 | 4:18 | 49.989
2019-11-03 | 4:18 | 49.992
2019-11-03 | 4:18 | 49.992
2019-11-03 | 4:18 | 49.992
2019-11-03 | 4:18 | 49.991
2019-11-03 | 4:18 | 49.991
2019-11-03 | 4:18 | 49.991
2019-11-03 | 4:18 | 49.991
2019-11-03 | 4:18 | 49.991
2019-11-03 | 4:18 | 49.992
2019-11-03 | 4:18 | 49.992
2019-11-03 | 4:18 | 49.992
2019-11-03 | 4:18 | 49.991
2019-11-03 | 4:19 | 49.99
2019-11-03 | 4:19 | 49.989
2019-11-03 | 4:19 | 49.988
2019-11-03 | 4:19 | 49.987
2019-11-03 | 4:19 | 49.986
2019-11-03 | 4:19 | 49.986
2019-11-03 | 4:19 | 49.986
2019-11-03 | 4:19 | 49.988
2019-11-03 | 4:19 | 49.99
2019-11-03 | 4:19 | 49.991
2019-11-03 | 4:19 | 49.992
2019-11-03 | 4:19 | 49.992
2019-11-03 | 4:19 | 49.991
2019-11-03 | 4:19 | 49.988
2019-11-03 | 4:19 | 49.986
2019-11-03 | 4:19 | 49.982
2019-11-03 | 4:19 | 49.976
2019-11-03 | 4:19 | 49.974
2019-11-03 | 4:19 | 49.97
2019-11-03 | 4:19 | 49.97
2019-11-03 | 4:19 | 49.97
2019-11-03 | 4:19 | 49.97
2019-11-03 | 4:19 | 49.971
2019-11-03 | 4:19 | 49.971
2019-11-03 | 4:19 | 49.974
2019-11-03 | 4:19 | 49.976
2019-11-03 | 4:19 | 49.977
2019-11-03 | 4:19 | 49.976
2019-11-03 | 4:19 | 49.974
2019-11-03 | 4:19 | 49.971
2019-11-03 | 4:19 | 49.971
2019-11-03 | 4:19 | 49.971
2019-11-03 | 4:19 | 49.974
2019-11-03 | 4:19 | 49.979
2019-11-03 | 4:19 | 49.982
2019-11-03 | 4:19 | 49.984
2019-11-03 | 4:19 | 49.972
2019-11-03 | 4:19 | 49.95
2019-11-03 | 4:19 | 49.928
2019-11-03 | 4:19 | 49.915
2019-11-03 | 4:19 | 49.907
2019-11-03 | 4:19 | 49.906
2019-11-03 | 4:19 | 49.909
2019-11-03 | 4:19 | 49.913
2019-11-03 | 4:19 | 49.918
2019-11-03 | 4:19 | 49.923
2019-11-03 | 4:19 | 49.927
2019-11-03 | 4:19 | 49.93
2019-11-03 | 4:19 | 49.932
2019-11-03 | 4:19 | 49.933
2019-11-03 | 4:19 | 49.934
2019-11-03 | 4:19 | 49.936
2019-11-03 | 4:19 | 49.936
2019-11-03 | 4:19 | 49.935
2019-11-03 | 4:19 | 49.934
2019-11-03 | 4:19 | 49.933
2019-11-03 | 4:19 | 49.934
2019-11-03 | 4:19 | 49.934
2019-11-03 | 4:19 | 49.932
2019-11-03 | 4:20 | 49.931
2019-11-03 | 4:20 | 49.929
2019-11-03 | 4:20 | 49.928
2019-11-03 | 4:20 | 49.928
2019-11-03 | 4:20 | 49.929
2019-11-03 | 4:20 | 49.928
2019-11-03 | 4:20 | 49.927
2019-11-03 | 4:20 | 49.924
2019-11-03 | 4:20 | 49.922
2019-11-03 | 4:20 | 49.921
2019-11-03 | 4:20 | 49.919
2019-11-03 | 4:20 | 49.919
2019-11-03 | 4:20 | 49.919
2019-11-03 | 4:20 | 49.919
2019-11-03 | 4:20 | 49.921
2019-11-03 | 4:20 | 49.922
2019-11-03 | 4:20 | 49.923
2019-11-03 | 4:20 | 49.924
2019-11-03 | 4:20 | 49.923
2019-11-03 | 4:20 | 49.923
2019-11-03 | 4:20 | 49.921
2019-11-03 | 4:20 | 49.921
2019-11-03 | 4:20 | 49.921
2019-11-03 | 4:20 | 49.921
2019-11-03 | 4:20 | 49.921
2019-11-03 | 4:20 | 49.923
2019-11-03 | 4:20 | 49.923
2019-11-03 | 4:20 | 49.924
2019-11-03 | 4:20 | 49.924
2019-11-03 | 4:20 | 49.926
2019-11-03 | 4:20 | 49.926
2019-11-03 | 4:20 | 49.925
2019-11-03 | 4:20 | 49.923
2019-11-03 | 4:20 | 49.921
2019-11-03 | 4:20 | 49.921
2019-11-03 | 4:20 | 49.921
2019-11-03 | 4:20 | 49.921
2019-11-03 | 4:20 | 49.921
2019-11-03 | 4:20 | 49.921
2019-11-03 | 4:20 | 49.923
2019-11-03 | 4:20 | 49.922
2019-11-03 | 4:20 | 49.922
2019-11-03 | 4:20 | 49.922
2019-11-03 | 4:20 | 49.92
2019-11-03 | 4:20 | 49.92
2019-11-03 | 4:20 | 49.92
2019-11-03 | 4:20 | 49.921
2019-11-03 | 4:20 | 49.917
2019-11-03 | 4:20 | 49.918
2019-11-03 | 4:20 | 49.915
2019-11-03 | 4:20 | 49.915
2019-11-03 | 4:20 | 49.914
2019-11-03 | 4:20 | 49.914
2019-11-03 | 4:20 | 49.913
2019-11-03 | 4:20 | 49.913
2019-11-03 | 4:20 | 49.912
2019-11-03 | 4:20 | 49.912
2019-11-03 | 4:20 | 49.91
2019-11-03 | 4:20 | 49.908
2019-11-03 | 4:20 | 49.906
2019-11-03 | 4:20 | 49.903
2019-11-03 | 4:21 | 49.902
2019-11-03 | 4:21 | 49.9
2019-11-03 | 4:21 | 49.901
2019-11-03 | 4:21 | 49.899
2019-11-03 | 4:21 | 49.897
2019-11-03 | 4:21 | 49.896
2019-11-03 | 4:21 | 49.893
2019-11-03 | 4:21 | 49.892
2019-11-03 | 4:21 | 49.891
2019-11-03 | 4:21 | 49.889
2019-11-03 | 4:21 | 49.89
2019-11-03 | 4:21 | 49.889
2019-11-03 | 4:21 | 49.889
2019-11-03 | 4:21 | 49.888
2019-11-03 | 4:21 | 49.889
2019-11-03 | 4:21 | 49.888
2019-11-03 | 4:21 | 49.888
2019-11-03 | 4:21 | 49.888
2019-11-03 | 4:21 | 49.887
2019-11-03 | 4:21 | 49.887
2019-11-03 | 4:21 | 49.886
2019-11-03 | 4:21 | 49.886
2019-11-03 | 4:21 | 49.885
2019-11-03 | 4:21 | 49.884
2019-11-03 | 4:21 | 49.885
2019-11-03 | 4:21 | 49.884
2019-11-03 | 4:21 | 49.884
2019-11-03 | 4:21 | 49.885
2019-11-03 | 4:21 | 49.886
2019-11-03 | 4:21 | 49.886
2019-11-03 | 4:21 | 49.885
2019-11-03 | 4:21 | 49.881
2019-11-03 | 4:21 | 49.874
2019-11-03 | 4:21 | 49.87
2019-11-03 | 4:21 | 49.867
2019-11-03 | 4:21 | 49.864
2019-11-03 | 4:21 | 49.858
2019-11-03 | 4:21 | 49.852
2019-11-03 | 4:21 | 49.845
2019-11-03 | 4:21 | 49.843
2019-11-03 | 4:21 | 49.835
2019-11-03 | 4:21 | 49.807
2019-11-03 | 4:21 | 49.787
2019-11-03 | 4:21 | 49.775
2019-11-03 | 4:21 | 49.769
2019-11-03 | 4:21 | 49.768
2019-11-03 | 4:21 | 49.771
2019-11-03 | 4:21 | 49.776
2019-11-03 | 4:21 | 49.78
2019-11-03 | 4:21 | 49.784
2019-11-03 | 4:21 | 49.788
2019-11-03 | 4:21 | 49.791
2019-11-03 | 4:21 | 49.793
2019-11-03 | 4:21 | 49.795
2019-11-03 | 4:21 | 49.796
2019-11-03 | 4:21 | 49.797
2019-11-03 | 4:21 | 49.799
2019-11-03 | 4:21 | 49.8
2019-11-03 | 4:21 | 49.798
2019-11-03 | 4:22 | 49.797
2019-11-03 | 4:22 | 49.796
2019-11-03 | 4:22 | 49.796
2019-11-03 | 4:22 | 49.797
2019-11-03 | 4:22 | 49.798
2019-11-03 | 4:22 | 49.8
2019-11-03 | 4:22 | 49.799
2019-11-03 | 4:22 | 49.8
2019-11-03 | 4:22 | 49.799
2019-11-03 | 4:22 | 49.797
2019-11-03 | 4:22 | 49.794
2019-11-03 | 4:22 | 49.791
2019-11-03 | 4:22 | 49.79
2019-11-03 | 4:22 | 49.791
2019-11-03 | 4:22 | 49.791
2019-11-03 | 4:22 | 49.793
2019-11-03 | 4:22 | 49.795
2019-11-03 | 4:22 | 49.797
2019-11-03 | 4:22 | 49.798
2019-11-03 | 4:22 | 49.801
2019-11-03 | 4:22 | 49.803
2019-11-03 | 4:22 | 49.805
2019-11-03 | 4:22 | 49.805
2019-11-03 | 4:22 | 49.805
2019-11-03 | 4:22 | 49.804
2019-11-03 | 4:22 | 49.802
2019-11-03 | 4:22 | 49.802
2019-11-03 | 4:22 | 49.801
2019-11-03 | 4:22 | 49.8
2019-11-03 | 4:22 | 49.801
2019-11-03 | 4:22 | 49.8
2019-11-03 | 4:22 | 49.799
2019-11-03 | 4:22 | 49.796
2019-11-03 | 4:22 | 49.797
2019-11-03 | 4:22 | 49.797
2019-11-03 | 4:22 | 49.796
2019-11-03 | 4:22 | 49.797
2019-11-03 | 4:22 | 49.796
2019-11-03 | 4:22 | 49.797
2019-11-03 | 4:22 | 49.799
2019-11-03 | 4:22 | 49.8
2019-11-03 | 4:22 | 49.802
2019-11-03 | 4:22 | 49.805
2019-11-03 | 4:22 | 49.806
2019-11-03 | 4:22 | 49.807
2019-11-03 | 4:22 | 49.807
2019-11-03 | 4:22 | 49.806
2019-11-03 | 4:22 | 49.805
2019-11-03 | 4:22 | 49.804
2019-11-03 | 4:22 | 49.801
2019-11-03 | 4:22 | 49.8
2019-11-03 | 4:22 | 49.799
2019-11-03 | 4:22 | 49.798
2019-11-03 | 4:22 | 49.799
2019-11-03 | 4:22 | 49.801
2019-11-03 | 4:22 | 49.803
2019-11-03 | 4:22 | 49.807
2019-11-03 | 4:22 | 49.81
2019-11-03 | 4:22 | 49.816
2019-11-03 | 4:22 | 49.822
2019-11-03 | 4:22 | 49.827
2019-11-03 | 4:23 | 49.834
2019-11-03 | 4:23 | 49.843
2019-11-03 | 4:23 | 49.851
2019-11-03 | 4:23 | 49.858
2019-11-03 | 4:23 | 49.862
2019-11-03 | 4:23 | 49.865
2019-11-03 | 4:23 | 49.864
2019-11-03 | 4:23 | 49.864
2019-11-03 | 4:23 | 49.865
2019-11-03 | 4:23 | 49.865
2019-11-03 | 4:23 | 49.866
2019-11-03 | 4:23 | 49.866
2019-11-03 | 4:23 | 49.866
2019-11-03 | 4:23 | 49.867
2019-11-03 | 4:23 | 49.867
2019-11-03 | 4:23 | 49.868
2019-11-03 | 4:23 | 49.868
2019-11-03 | 4:23 | 49.868
2019-11-03 | 4:23 | 49.868
2019-11-03 | 4:23 | 49.868
2019-11-03 | 4:23 | 49.869
2019-11-03 | 4:23 | 49.87
2019-11-03 | 4:23 | 49.872
2019-11-03 | 4:23 | 49.874
2019-11-03 | 4:23 | 49.876
2019-11-03 | 4:23 | 49.877
2019-11-03 | 4:23 | 49.876
2019-11-03 | 4:23 | 49.878
2019-11-03 | 4:23 | 49.881
2019-11-03 | 4:23 | 49.881
2019-11-03 | 4:23 | 49.881
2019-11-03 | 4:23 | 49.884
2019-11-03 | 4:23 | 49.885
2019-11-03 | 4:23 | 49.886
2019-11-03 | 4:23 | 49.887
2019-11-03 | 4:23 | 49.887
2019-11-03 | 4:23 | 49.888
2019-11-03 | 4:23 | 49.887
2019-11-03 | 4:23 | 49.887
2019-11-03 | 4:23 | 49.888
2019-11-03 | 4:23 | 49.888
2019-11-03 | 4:23 | 49.887
2019-11-03 | 4:23 | 49.886
2019-11-03 | 4:23 | 49.887
2019-11-03 | 4:23 | 49.888
2019-11-03 | 4:23 | 49.89
2019-11-03 | 4:23 | 49.89
2019-11-03 | 4:23 | 49.889
2019-11-03 | 4:23 | 49.889
2019-11-03 | 4:23 | 49.89
2019-11-03 | 4:23 | 49.889
2019-11-03 | 4:23 | 49.89
2019-11-03 | 4:23 | 49.89
2019-11-03 | 4:23 | 49.892
2019-11-03 | 4:23 | 49.893
2019-11-03 | 4:23 | 49.894
2019-11-03 | 4:23 | 49.892
2019-11-03 | 4:23 | 49.895
2019-11-03 | 4:23 | 49.896
2019-11-03 | 4:24 | 49.897
2019-11-03 | 4:24 | 49.898
2019-11-03 | 4:24 | 49.896
2019-11-03 | 4:24 | 49.896
2019-11-03 | 4:24 | 49.896
2019-11-03 | 4:24 | 49.895
2019-11-03 | 4:24 | 49.893
2019-11-03 | 4:24 | 49.892
2019-11-03 | 4:24 | 49.892
2019-11-03 | 4:24 | 49.893
2019-11-03 | 4:24 | 49.891
2019-11-03 | 4:24 | 49.895
2019-11-03 | 4:24 | 49.897
2019-11-03 | 4:24 | 49.899
2019-11-03 | 4:24 | 49.9
2019-11-03 | 4:24 | 49.902
2019-11-03 | 4:24 | 49.902
2019-11-03 | 4:24 | 49.902
2019-11-03 | 4:24 | 49.9
2019-11-03 | 4:24 | 49.9
2019-11-03 | 4:24 | 49.9
2019-11-03 | 4:24 | 49.9
2019-11-03 | 4:24 | 49.9
2019-11-03 | 4:24 | 49.902
2019-11-03 | 4:24 | 49.903
2019-11-03 | 4:24 | 49.902
2019-11-03 | 4:24 | 49.904
2019-11-03 | 4:24 | 49.903
2019-11-03 | 4:24 | 49.903
2019-11-03 | 4:24 | 49.904
2019-11-03 | 4:24 | 49.903
2019-11-03 | 4:24 | 49.904
2019-11-03 | 4:24 | 49.905
2019-11-03 | 4:24 | 49.903
2019-11-03 | 4:24 | 49.903
2019-11-03 | 4:24 | 49.903
2019-11-03 | 4:24 | 49.902
2019-11-03 | 4:24 | 49.902
2019-11-03 | 4:24 | 49.902
2019-11-03 | 4:24 | 49.903
2019-11-03 | 4:24 | 49.904
2019-11-03 | 4:24 | 49.905
2019-11-03 | 4:24 | 49.906
2019-11-03 | 4:24 | 49.908
2019-11-03 | 4:24 | 49.909
2019-11-03 | 4:24 | 49.911
2019-11-03 | 4:24 | 49.913
2019-11-03 | 4:24 | 49.916
2019-11-03 | 4:24 | 49.916
2019-11-03 | 4:24 | 49.916
2019-11-03 | 4:24 | 49.918
2019-11-03 | 4:24 | 49.917
2019-11-03 | 4:24 | 49.917
2019-11-03 | 4:24 | 49.916
2019-11-03 | 4:24 | 49.915
2019-11-03 | 4:24 | 49.913
2019-11-03 | 4:24 | 49.913
2019-11-03 | 4:24 | 49.913
2019-11-03 | 4:24 | 49.913
2019-11-03 | 4:24 | 49.914
2019-11-03 | 4:24 | 49.914
2019-11-03 | 4:25 | 49.914
2019-11-03 | 4:25 | 49.915
2019-11-03 | 4:25 | 49.915
2019-11-03 | 4:25 | 49.913
2019-11-03 | 4:25 | 49.912
2019-11-03 | 4:25 | 49.913
2019-11-03 | 4:25 | 49.911
2019-11-03 | 4:25 | 49.911
2019-11-03 | 4:25 | 49.91
2019-11-03 | 4:25 | 49.91
2019-11-03 | 4:25 | 49.911
2019-11-03 | 4:25 | 49.911
2019-11-03 | 4:25 | 49.913
2019-11-03 | 4:25 | 49.914
2019-11-03 | 4:25 | 49.916
2019-11-03 | 4:25 | 49.919
2019-11-03 | 4:25 | 49.923
2019-11-03 | 4:25 | 49.929
2019-11-03 | 4:25 | 49.928
2019-11-03 | 4:25 | 49.927
2019-11-03 | 4:25 | 49.924
2019-11-03 | 4:25 | 49.92
2019-11-03 | 4:25 | 49.918
2019-11-03 | 4:25 | 49.916
2019-11-03 | 4:25 | 49.913
2019-11-03 | 4:25 | 49.913
2019-11-03 | 4:25 | 49.913
2019-11-03 | 4:25 | 49.914
2019-11-03 | 4:25 | 49.913
2019-11-03 | 4:25 | 49.913
2019-11-03 | 4:25 | 49.914
2019-11-03 | 4:25 | 49.914
2019-11-03 | 4:25 | 49.913
2019-11-03 | 4:25 | 49.915
2019-11-03 | 4:25 | 49.914
2019-11-03 | 4:25 | 49.914
2019-11-03 | 4:25 | 49.913
2019-11-03 | 4:25 | 49.914
2019-11-03 | 4:25 | 49.914
2019-11-03 | 4:25 | 49.915
2019-11-03 | 4:25 | 49.915
2019-11-03 | 4:25 | 49.915
2019-11-03 | 4:25 | 49.915
2019-11-03 | 4:25 | 49.913
2019-11-03 | 4:25 | 49.912
2019-11-03 | 4:25 | 49.91
2019-11-03 | 4:25 | 49.91
2019-11-03 | 4:25 | 49.909
2019-11-03 | 4:25 | 49.909
2019-11-03 | 4:25 | 49.908
2019-11-03 | 4:25 | 49.908
2019-11-03 | 4:25 | 49.908
2019-11-03 | 4:25 | 49.91
2019-11-03 | 4:25 | 49.913
2019-11-03 | 4:25 | 49.915
2019-11-03 | 4:25 | 49.917
2019-11-03 | 4:25 | 49.919
2019-11-03 | 4:25 | 49.922
2019-11-03 | 4:25 | 49.92
2019-11-03 | 4:26 | 49.92
2019-11-03 | 4:26 | 49.917
2019-11-03 | 4:26 | 49.917
2019-11-03 | 4:26 | 49.916
2019-11-03 | 4:26 | 49.919
2019-11-03 | 4:26 | 49.92
2019-11-03 | 4:26 | 49.92
2019-11-03 | 4:26 | 49.92
2019-11-03 | 4:26 | 49.921
2019-11-03 | 4:26 | 49.922
2019-11-03 | 4:26 | 49.923
2019-11-03 | 4:26 | 49.923
2019-11-03 | 4:26 | 49.922
2019-11-03 | 4:26 | 49.921
2019-11-03 | 4:26 | 49.919
2019-11-03 | 4:26 | 49.921
2019-11-03 | 4:26 | 49.923
2019-11-03 | 4:26 | 49.926
2019-11-03 | 4:26 | 49.927
2019-11-03 | 4:26 | 49.929
2019-11-03 | 4:26 | 49.933
2019-11-03 | 4:26 | 49.937
2019-11-03 | 4:26 | 49.938
2019-11-03 | 4:26 | 49.937
2019-11-03 | 4:26 | 49.934
2019-11-03 | 4:26 | 49.931
2019-11-03 | 4:26 | 49.929
2019-11-03 | 4:26 | 49.929
2019-11-03 | 4:26 | 49.932
2019-11-03 | 4:26 | 49.934
2019-11-03 | 4:26 | 49.933
2019-11-03 | 4:26 | 49.931
2019-11-03 | 4:26 | 49.926
2019-11-03 | 4:26 | 49.923
2019-11-03 | 4:26 | 49.924
2019-11-03 | 4:26 | 49.923
2019-11-03 | 4:26 | 49.92
2019-11-03 | 4:26 | 49.919
2019-11-03 | 4:26 | 49.918
2019-11-03 | 4:26 | 49.917
2019-11-03 | 4:26 | 49.918
2019-11-03 | 4:26 | 49.919
2019-11-03 | 4:26 | 49.92
2019-11-03 | 4:26 | 49.921
2019-11-03 | 4:26 | 49.923
2019-11-03 | 4:26 | 49.923
2019-11-03 | 4:26 | 49.926
2019-11-03 | 4:26 | 49.929
2019-11-03 | 4:26 | 49.931
2019-11-03 | 4:26 | 49.931
2019-11-03 | 4:26 | 49.931
2019-11-03 | 4:26 | 49.93
2019-11-03 | 4:26 | 49.928
2019-11-03 | 4:26 | 49.925
2019-11-03 | 4:26 | 49.923
2019-11-03 | 4:26 | 49.919
2019-11-03 | 4:26 | 49.917
2019-11-03 | 4:26 | 49.917
2019-11-03 | 4:26 | 49.917
2019-11-03 | 4:26 | 49.919
2019-11-03 | 4:26 | 49.92
2019-11-03 | 4:27 | 49.923
2019-11-03 | 4:27 | 49.924
2019-11-03 | 4:27 | 49.926
2019-11-03 | 4:27 | 49.927
2019-11-03 | 4:27 | 49.927
2019-11-03 | 4:27 | 49.927
2019-11-03 | 4:27 | 49.926
2019-11-03 | 4:27 | 49.927
2019-11-03 | 4:27 | 49.928
2019-11-03 | 4:27 | 49.928
2019-11-03 | 4:27 | 49.928
2019-11-03 | 4:27 | 49.929
2019-11-03 | 4:27 | 49.928
2019-11-03 | 4:27 | 49.927
2019-11-03 | 4:27 | 49.927
2019-11-03 | 4:27 | 49.927
2019-11-03 | 4:27 | 49.927
2019-11-03 | 4:27 | 49.927
2019-11-03 | 4:27 | 49.926
2019-11-03 | 4:27 | 49.926
2019-11-03 | 4:27 | 49.926
2019-11-03 | 4:27 | 49.926
2019-11-03 | 4:27 | 49.926
2019-11-03 | 4:27 | 49.926
2019-11-03 | 4:27 | 49.927
2019-11-03 | 4:27 | 49.926
2019-11-03 | 4:27 | 49.926
2019-11-03 | 4:27 | 49.925
2019-11-03 | 4:27 | 49.924
2019-11-03 | 4:27 | 49.924
2019-11-03 | 4:27 | 49.921
2019-11-03 | 4:27 | 49.918
2019-11-03 | 4:27 | 49.916
2019-11-03 | 4:27 | 49.917
2019-11-03 | 4:27 | 49.918
2019-11-03 | 4:27 | 49.918
2019-11-03 | 4:27 | 49.92
2019-11-03 | 4:27 | 49.922
2019-11-03 | 4:27 | 49.925
2019-11-03 | 4:27 | 49.926
2019-11-03 | 4:27 | 49.926
2019-11-03 | 4:27 | 49.925
2019-11-03 | 4:27 | 49.924
2019-11-03 | 4:27 | 49.924
2019-11-03 | 4:27 | 49.926
2019-11-03 | 4:27 | 49.929
2019-11-03 | 4:27 | 49.937
2019-11-03 | 4:27 | 49.946
2019-11-03 | 4:27 | 49.951
2019-11-03 | 4:27 | 49.954
2019-11-03 | 4:27 | 49.955
2019-11-03 | 4:27 | 49.953
2019-11-03 | 4:27 | 49.95
2019-11-03 | 4:27 | 49.947
2019-11-03 | 4:27 | 49.945
2019-11-03 | 4:27 | 49.943
2019-11-03 | 4:27 | 49.94
2019-11-03 | 4:27 | 49.935
2019-11-03 | 4:27 | 49.931
2019-11-03 | 4:27 | 49.928
2019-11-03 | 4:28 | 49.927
2019-11-03 | 4:28 | 49.927
2019-11-03 | 4:28 | 49.928
2019-11-03 | 4:28 | 49.929
2019-11-03 | 4:28 | 49.929
2019-11-03 | 4:28 | 49.93
2019-11-03 | 4:28 | 49.931
2019-11-03 | 4:28 | 49.931
2019-11-03 | 4:28 | 49.93
2019-11-03 | 4:28 | 49.929
2019-11-03 | 4:28 | 49.928
2019-11-03 | 4:28 | 49.929
2019-11-03 | 4:28 | 49.931
2019-11-03 | 4:28 | 49.935
2019-11-03 | 4:28 | 49.938
2019-11-03 | 4:28 | 49.939
2019-11-03 | 4:28 | 49.938
2019-11-03 | 4:28 | 49.936
2019-11-03 | 4:28 | 49.936
2019-11-03 | 4:28 | 49.936
2019-11-03 | 4:28 | 49.936
2019-11-03 | 4:28 | 49.935
2019-11-03 | 4:28 | 49.936
2019-11-03 | 4:28 | 49.937
2019-11-03 | 4:28 | 49.936
2019-11-03 | 4:28 | 49.935
2019-11-03 | 4:28 | 49.935
2019-11-03 | 4:28 | 49.936
2019-11-03 | 4:28 | 49.935
2019-11-03 | 4:28 | 49.934
2019-11-03 | 4:28 | 49.933
2019-11-03 | 4:28 | 49.936
2019-11-03 | 4:28 | 49.938
2019-11-03 | 4:28 | 49.94
2019-11-03 | 4:28 | 49.941
2019-11-03 | 4:28 | 49.94
2019-11-03 | 4:28 | 49.941
2019-11-03 | 4:28 | 49.942
2019-11-03 | 4:28 | 49.941
2019-11-03 | 4:28 | 49.94
2019-11-03 | 4:28 | 49.936
2019-11-03 | 4:28 | 49.933
2019-11-03 | 4:28 | 49.931
2019-11-03 | 4:28 | 49.931
2019-11-03 | 4:28 | 49.93
2019-11-03 | 4:28 | 49.93
2019-11-03 | 4:28 | 49.93
2019-11-03 | 4:28 | 49.93
2019-11-03 | 4:28 | 49.931
2019-11-03 | 4:28 | 49.931
2019-11-03 | 4:28 | 49.932
2019-11-03 | 4:28 | 49.932
2019-11-03 | 4:28 | 49.933
2019-11-03 | 4:28 | 49.934
2019-11-03 | 4:28 | 49.938
2019-11-03 | 4:28 | 49.94
2019-11-03 | 4:28 | 49.94
2019-11-03 | 4:28 | 49.939
2019-11-03 | 4:28 | 49.938
2019-11-03 | 4:28 | 49.936
2019-11-03 | 4:29 | 49.933
2019-11-03 | 4:29 | 49.932
2019-11-03 | 4:29 | 49.931
2019-11-03 | 4:29 | 49.931
2019-11-03 | 4:29 | 49.932
2019-11-03 | 4:29 | 49.933
2019-11-03 | 4:29 | 49.936
2019-11-03 | 4:29 | 49.938
2019-11-03 | 4:29 | 49.94
2019-11-03 | 4:29 | 49.944
2019-11-03 | 4:29 | 49.945
2019-11-03 | 4:29 | 49.946
2019-11-03 | 4:29 | 49.946
2019-11-03 | 4:29 | 49.949
2019-11-03 | 4:29 | 49.952
2019-11-03 | 4:29 | 49.953
2019-11-03 | 4:29 | 49.952
2019-11-03 | 4:29 | 49.949
2019-11-03 | 4:29 | 49.946
2019-11-03 | 4:29 | 49.943
2019-11-03 | 4:29 | 49.94
2019-11-03 | 4:29 | 49.938
2019-11-03 | 4:29 | 49.938
2019-11-03 | 4:29 | 49.938
2019-11-03 | 4:29 | 49.937
2019-11-03 | 4:29 | 49.937
2019-11-03 | 4:29 | 49.938
2019-11-03 | 4:29 | 49.939
2019-11-03 | 4:29 | 49.94
2019-11-03 | 4:29 | 49.94
2019-11-03 | 4:29 | 49.941
2019-11-03 | 4:29 | 49.94
2019-11-03 | 4:29 | 49.94
2019-11-03 | 4:29 | 49.94
2019-11-03 | 4:29 | 49.941
2019-11-03 | 4:29 | 49.94
2019-11-03 | 4:29 | 49.937
2019-11-03 | 4:29 | 49.935
2019-11-03 | 4:29 | 49.934
2019-11-03 | 4:29 | 49.93
2019-11-03 | 4:29 | 49.929
2019-11-03 | 4:29 | 49.928
2019-11-03 | 4:29 | 49.926
2019-11-03 | 4:29 | 49.925
2019-11-03 | 4:29 | 49.922
2019-11-03 | 4:29 | 49.92
2019-11-03 | 4:29 | 49.919
2019-11-03 | 4:29 | 49.92
2019-11-03 | 4:29 | 49.919
2019-11-03 | 4:29 | 49.917
2019-11-03 | 4:29 | 49.915
2019-11-03 | 4:29 | 49.915
2019-11-03 | 4:29 | 49.917
2019-11-03 | 4:29 | 49.921
2019-11-03 | 4:29 | 49.925
2019-11-03 | 4:29 | 49.927
2019-11-03 | 4:29 | 49.926
2019-11-03 | 4:29 | 49.927
2019-11-03 | 4:29 | 49.926
2019-11-03 | 4:29 | 49.925
2019-11-03 | 4:30 | 49.923
2019-11-03 | 4:30 | 49.919
2019-11-03 | 4:30 | 49.916
2019-11-03 | 4:30 | 49.915
2019-11-03 | 4:30 | 49.913
2019-11-03 | 4:30 | 49.913
2019-11-03 | 4:30 | 49.913
2019-11-03 | 4:30 | 49.912
2019-11-03 | 4:30 | 49.912
2019-11-03 | 4:30 | 49.913
2019-11-03 | 4:30 | 49.913
2019-11-03 | 4:30 | 49.913
2019-11-03 | 4:30 | 49.915
2019-11-03 | 4:30 | 49.916
2019-11-03 | 4:30 | 49.917
2019-11-03 | 4:30 | 49.917
2019-11-03 | 4:30 | 49.916
2019-11-03 | 4:30 | 49.915
2019-11-03 | 4:30 | 49.914
2019-11-03 | 4:30 | 49.911
2019-11-03 | 4:30 | 49.907
2019-11-03 | 4:30 | 49.904
2019-11-03 | 4:30 | 49.904
2019-11-03 | 4:30 | 49.904
2019-11-03 | 4:30 | 49.905
2019-11-03 | 4:30 | 49.906
2019-11-03 | 4:30 | 49.908
2019-11-03 | 4:30 | 49.909
2019-11-03 | 4:30 | 49.91
2019-11-03 | 4:30 | 49.91
2019-11-03 | 4:30 | 49.908
2019-11-03 | 4:30 | 49.904
2019-11-03 | 4:30 | 49.904
2019-11-03 | 4:30 | 49.906
2019-11-03 | 4:30 | 49.909
2019-11-03 | 4:30 | 49.912
2019-11-03 | 4:30 | 49.914
2019-11-03 | 4:30 | 49.915
2019-11-03 | 4:30 | 49.915
2019-11-03 | 4:30 | 49.915
2019-11-03 | 4:30 | 49.913
2019-11-03 | 4:30 | 49.911
2019-11-03 | 4:30 | 49.91
2019-11-03 | 4:30 | 49.91
2019-11-03 | 4:30 | 49.909
2019-11-03 | 4:30 | 49.908
2019-11-03 | 4:30 | 49.906
2019-11-03 | 4:30 | 49.904
2019-11-03 | 4:30 | 49.903
2019-11-03 | 4:30 | 49.902
2019-11-03 | 4:30 | 49.905
2019-11-03 | 4:30 | 49.905
2019-11-03 | 4:30 | 49.907
2019-11-03 | 4:30 | 49.906
2019-11-03 | 4:30 | 49.907
2019-11-03 | 4:30 | 49.907
2019-11-03 | 4:30 | 49.909
2019-11-03 | 4:30 | 49.91
2019-11-03 | 4:30 | 49.911
2019-11-03 | 4:30 | 49.91
2019-11-03 | 4:31 | 49.908
2019-11-03 | 4:31 | 49.907
2019-11-03 | 4:31 | 49.906
2019-11-03 | 4:31 | 49.906
2019-11-03 | 4:31 | 49.906
2019-11-03 | 4:31 | 49.905
2019-11-03 | 4:31 | 49.905
2019-11-03 | 4:31 | 49.905
2019-11-03 | 4:31 | 49.905
2019-11-03 | 4:31 | 49.904
2019-11-03 | 4:31 | 49.904
2019-11-03 | 4:31 | 49.901
2019-11-03 | 4:31 | 49.9
2019-11-03 | 4:31 | 49.897
2019-11-03 | 4:31 | 49.896
2019-11-03 | 4:31 | 49.894
2019-11-03 | 4:31 | 49.896
2019-11-03 | 4:31 | 49.897
2019-11-03 | 4:31 | 49.895
2019-11-03 | 4:31 | 49.894
2019-11-03 | 4:31 | 49.894
2019-11-03 | 4:31 | 49.894
2019-11-03 | 4:31 | 49.893
2019-11-03 | 4:31 | 49.892
2019-11-03 | 4:31 | 49.888
2019-11-03 | 4:31 | 49.885
2019-11-03 | 4:31 | 49.884
2019-11-03 | 4:31 | 49.883
2019-11-03 | 4:31 | 49.886
2019-11-03 | 4:31 | 49.888
2019-11-03 | 4:31 | 49.888
2019-11-03 | 4:31 | 49.888
2019-11-03 | 4:31 | 49.888
2019-11-03 | 4:31 | 49.888
2019-11-03 | 4:31 | 49.886
2019-11-03 | 4:31 | 49.887
2019-11-03 | 4:31 | 49.886
2019-11-03 | 4:31 | 49.885
2019-11-03 | 4:31 | 49.883
2019-11-03 | 4:31 | 49.884
2019-11-03 | 4:31 | 49.883
2019-11-03 | 4:31 | 49.882
2019-11-03 | 4:31 | 49.881
2019-11-03 | 4:31 | 49.88
2019-11-03 | 4:31 | 49.879
2019-11-03 | 4:31 | 49.879
2019-11-03 | 4:31 | 49.877
2019-11-03 | 4:31 | 49.879
2019-11-03 | 4:31 | 49.881
2019-11-03 | 4:31 | 49.881
2019-11-03 | 4:31 | 49.88
2019-11-03 | 4:31 | 49.88
2019-11-03 | 4:31 | 49.881
2019-11-03 | 4:31 | 49.882
2019-11-03 | 4:31 | 49.883
2019-11-03 | 4:31 | 49.882
2019-11-03 | 4:31 | 49.883
2019-11-03 | 4:31 | 49.88
2019-11-03 | 4:31 | 49.878
2019-11-03 | 4:32 | 49.877
2019-11-03 | 4:32 | 49.875
2019-11-03 | 4:32 | 49.875
2019-11-03 | 4:32 | 49.876
2019-11-03 | 4:32 | 49.877
2019-11-03 | 4:32 | 49.877
2019-11-03 | 4:32 | 49.879
2019-11-03 | 4:32 | 49.879
2019-11-03 | 4:32 | 49.879
2019-11-03 | 4:32 | 49.878
2019-11-03 | 4:32 | 49.878
2019-11-03 | 4:32 | 49.879
2019-11-03 | 4:32 | 49.878
2019-11-03 | 4:32 | 49.879
2019-11-03 | 4:32 | 49.88
2019-11-03 | 4:32 | 49.881
2019-11-03 | 4:32 | 49.88
2019-11-03 | 4:32 | 49.879
2019-11-03 | 4:32 | 49.878
2019-11-03 | 4:32 | 49.88
2019-11-03 | 4:32 | 49.883
2019-11-03 | 4:32 | 49.885
2019-11-03 | 4:32 | 49.886
2019-11-03 | 4:32 | 49.885
2019-11-03 | 4:32 | 49.886
2019-11-03 | 4:32 | 49.887
2019-11-03 | 4:32 | 49.886
2019-11-03 | 4:32 | 49.884
2019-11-03 | 4:32 | 49.884
2019-11-03 | 4:32 | 49.882
2019-11-03 | 4:32 | 49.883
2019-11-03 | 4:32 | 49.885
2019-11-03 | 4:32 | 49.886
2019-11-03 | 4:32 | 49.887
2019-11-03 | 4:32 | 49.888
2019-11-03 | 4:32 | 49.89
2019-11-03 | 4:32 | 49.889
2019-11-03 | 4:32 | 49.888
2019-11-03 | 4:32 | 49.891
2019-11-03 | 4:32 | 49.892
2019-11-03 | 4:32 | 49.894
2019-11-03 | 4:32 | 49.896
2019-11-03 | 4:32 | 49.896
2019-11-03 | 4:32 | 49.896
2019-11-03 | 4:32 | 49.896
2019-11-03 | 4:32 | 49.895
2019-11-03 | 4:32 | 49.892
2019-11-03 | 4:32 | 49.889
2019-11-03 | 4:32 | 49.886
2019-11-03 | 4:32 | 49.883
2019-11-03 | 4:32 | 49.878
2019-11-03 | 4:32 | 49.874
2019-11-03 | 4:32 | 49.872
2019-11-03 | 4:32 | 49.87
2019-11-03 | 4:32 | 49.869
2019-11-03 | 4:32 | 49.869
2019-11-03 | 4:32 | 49.872
2019-11-03 | 4:32 | 49.876
2019-11-03 | 4:32 | 49.879
2019-11-03 | 4:32 | 49.881
2019-11-03 | 4:33 | 49.88
2019-11-03 | 4:33 | 49.879
2019-11-03 | 4:33 | 49.878
2019-11-03 | 4:33 | 49.874
2019-11-03 | 4:33 | 49.872
2019-11-03 | 4:33 | 49.869
2019-11-03 | 4:33 | 49.865
2019-11-03 | 4:33 | 49.863
2019-11-03 | 4:33 | 49.863
2019-11-03 | 4:33 | 49.866
2019-11-03 | 4:33 | 49.868
2019-11-03 | 4:33 | 49.87
2019-11-03 | 4:33 | 49.872
2019-11-03 | 4:33 | 49.874
2019-11-03 | 4:33 | 49.876
2019-11-03 | 4:33 | 49.878
2019-11-03 | 4:33 | 49.878
2019-11-03 | 4:33 | 49.877
2019-11-03 | 4:33 | 49.876
2019-11-03 | 4:33 | 49.874
2019-11-03 | 4:33 | 49.872
2019-11-03 | 4:33 | 49.871
2019-11-03 | 4:33 | 49.869
2019-11-03 | 4:33 | 49.868
2019-11-03 | 4:33 | 49.867
2019-11-03 | 4:33 | 49.868
2019-11-03 | 4:33 | 49.868
2019-11-03 | 4:33 | 49.871
2019-11-03 | 4:33 | 49.874
2019-11-03 | 4:33 | 49.875
2019-11-03 | 4:33 | 49.873
2019-11-03 | 4:33 | 49.872
2019-11-03 | 4:33 | 49.871
2019-11-03 | 4:33 | 49.871
2019-11-03 | 4:33 | 49.871
2019-11-03 | 4:33 | 49.87
2019-11-03 | 4:33 | 49.869
2019-11-03 | 4:33 | 49.867
2019-11-03 | 4:33 | 49.865
2019-11-03 | 4:33 | 49.864
2019-11-03 | 4:33 | 49.863
2019-11-03 | 4:33 | 49.864
2019-11-03 | 4:33 | 49.864
2019-11-03 | 4:33 | 49.865
2019-11-03 | 4:33 | 49.867
2019-11-03 | 4:33 | 49.869
2019-11-03 | 4:33 | 49.868
2019-11-03 | 4:33 | 49.869
2019-11-03 | 4:33 | 49.868
2019-11-03 | 4:33 | 49.869
2019-11-03 | 4:33 | 49.87
2019-11-03 | 4:33 | 49.872
2019-11-03 | 4:33 | 49.872
2019-11-03 | 4:33 | 49.873
2019-11-03 | 4:33 | 49.874
2019-11-03 | 4:33 | 49.875
2019-11-03 | 4:33 | 49.876
2019-11-03 | 4:33 | 49.877
2019-11-03 | 4:33 | 49.878
2019-11-03 | 4:33 | 49.879
2019-11-03 | 4:34 | 49.878
2019-11-03 | 4:34 | 49.878
2019-11-03 | 4:34 | 49.878
2019-11-03 | 4:34 | 49.879
2019-11-03 | 4:34 | 49.879
2019-11-03 | 4:34 | 49.881
2019-11-03 | 4:34 | 49.882
2019-11-03 | 4:34 | 49.886
2019-11-03 | 4:34 | 49.887
2019-11-03 | 4:34 | 49.89
2019-11-03 | 4:34 | 49.89
2019-11-03 | 4:34 | 49.89
2019-11-03 | 4:34 | 49.891
2019-11-03 | 4:34 | 49.892
2019-11-03 | 4:34 | 49.897
2019-11-03 | 4:34 | 49.901
2019-11-03 | 4:34 | 49.902
2019-11-03 | 4:34 | 49.9
2019-11-03 | 4:34 | 49.898
2019-11-03 | 4:34 | 49.897
2019-11-03 | 4:34 | 49.896
2019-11-03 | 4:34 | 49.893
2019-11-03 | 4:34 | 49.891
2019-11-03 | 4:34 | 49.889
2019-11-03 | 4:34 | 49.887
2019-11-03 | 4:34 | 49.885
2019-11-03 | 4:34 | 49.884
2019-11-03 | 4:34 | 49.882
2019-11-03 | 4:34 | 49.879
2019-11-03 | 4:34 | 49.878
2019-11-03 | 4:34 | 49.878
2019-11-03 | 4:34 | 49.875
2019-11-03 | 4:34 | 49.878
2019-11-03 | 4:34 | 49.879
2019-11-03 | 4:34 | 49.88
2019-11-03 | 4:34 | 49.879
2019-11-03 | 4:34 | 49.878
2019-11-03 | 4:34 | 49.88
2019-11-03 | 4:34 | 49.881
2019-11-03 | 4:34 | 49.878
2019-11-03 | 4:34 | 49.872
2019-11-03 | 4:34 | 49.866
2019-11-03 | 4:34 | 49.862
2019-11-03 | 4:34 | 49.863
2019-11-03 | 4:34 | 49.865
2019-11-03 | 4:34 | 49.869
2019-11-03 | 4:34 | 49.871
2019-11-03 | 4:34 | 49.873
2019-11-03 | 4:34 | 49.873
2019-11-03 | 4:34 | 49.874
2019-11-03 | 4:34 | 49.876
2019-11-03 | 4:34 | 49.876
2019-11-03 | 4:34 | 49.876
2019-11-03 | 4:34 | 49.873
2019-11-03 | 4:34 | 49.872
2019-11-03 | 4:34 | 49.873
2019-11-03 | 4:34 | 49.873
2019-11-03 | 4:34 | 49.873
2019-11-03 | 4:34 | 49.87
2019-11-03 | 4:34 | 49.869
2019-11-03 | 4:34 | 49.87
2019-11-03 | 4:35 | 49.874
2019-11-03 | 4:35 | 49.877
2019-11-03 | 4:35 | 49.881
2019-11-03 | 4:35 | 49.887
2019-11-03 | 4:35 | 49.892
2019-11-03 | 4:35 | 49.893
2019-11-03 | 4:35 | 49.893
2019-11-03 | 4:35 | 49.892
2019-11-03 | 4:35 | 49.891
2019-11-03 | 4:35 | 49.888
2019-11-03 | 4:35 | 49.885
2019-11-03 | 4:35 | 49.88
2019-11-03 | 4:35 | 49.877
2019-11-03 | 4:35 | 49.873
2019-11-03 | 4:35 | 49.871
2019-11-03 | 4:35 | 49.87
2019-11-03 | 4:35 | 49.869
2019-11-03 | 4:35 | 49.867
2019-11-03 | 4:35 | 49.866
2019-11-03 | 4:35 | 49.867
2019-11-03 | 4:35 | 49.869
2019-11-03 | 4:35 | 49.872
2019-11-03 | 4:35 | 49.873
2019-11-03 | 4:35 | 49.876
2019-11-03 | 4:35 | 49.878
2019-11-03 | 4:35 | 49.883
2019-11-03 | 4:35 | 49.885
2019-11-03 | 4:35 | 49.887
2019-11-03 | 4:35 | 49.89
2019-11-03 | 4:35 | 49.889
2019-11-03 | 4:35 | 49.889
2019-11-03 | 4:35 | 49.89
2019-11-03 | 4:35 | 49.891
2019-11-03 | 4:35 | 49.891
2019-11-03 | 4:35 | 49.891
2019-11-03 | 4:35 | 49.892
2019-11-03 | 4:35 | 49.892
2019-11-03 | 4:35 | 49.89
2019-11-03 | 4:35 | 49.887
2019-11-03 | 4:35 | 49.884
2019-11-03 | 4:35 | 49.882
2019-11-03 | 4:35 | 49.881
2019-11-03 | 4:35 | 49.879
2019-11-03 | 4:35 | 49.879
2019-11-03 | 4:35 | 49.88
2019-11-03 | 4:35 | 49.879
2019-11-03 | 4:35 | 49.879
2019-11-03 | 4:35 | 49.88
2019-11-03 | 4:35 | 49.883
2019-11-03 | 4:35 | 49.884
2019-11-03 | 4:35 | 49.886
2019-11-03 | 4:35 | 49.89
2019-11-03 | 4:35 | 49.896
2019-11-03 | 4:35 | 49.899
2019-11-03 | 4:35 | 49.903
2019-11-03 | 4:35 | 49.905
2019-11-03 | 4:35 | 49.905
2019-11-03 | 4:35 | 49.904
2019-11-03 | 4:35 | 49.902
2019-11-03 | 4:36 | 49.9
2019-11-03 | 4:36 | 49.898
2019-11-03 | 4:36 | 49.896
2019-11-03 | 4:36 | 49.894
2019-11-03 | 4:36 | 49.894
2019-11-03 | 4:36 | 49.895
2019-11-03 | 4:36 | 49.898
2019-11-03 | 4:36 | 49.902
2019-11-03 | 4:36 | 49.905
2019-11-03 | 4:36 | 49.906
2019-11-03 | 4:36 | 49.906
2019-11-03 | 4:36 | 49.905
2019-11-03 | 4:36 | 49.905
2019-11-03 | 4:36 | 49.904
2019-11-03 | 4:36 | 49.9
2019-11-03 | 4:36 | 49.895
2019-11-03 | 4:36 | 49.892
2019-11-03 | 4:36 | 49.89
2019-11-03 | 4:36 | 49.89
2019-11-03 | 4:36 | 49.892
2019-11-03 | 4:36 | 49.894
2019-11-03 | 4:36 | 49.895
2019-11-03 | 4:36 | 49.897
2019-11-03 | 4:36 | 49.897
2019-11-03 | 4:36 | 49.897
2019-11-03 | 4:36 | 49.898
2019-11-03 | 4:36 | 49.896
2019-11-03 | 4:36 | 49.895
2019-11-03 | 4:36 | 49.893
2019-11-03 | 4:36 | 49.893
2019-11-03 | 4:36 | 49.891
2019-11-03 | 4:36 | 49.892
2019-11-03 | 4:36 | 49.892
2019-11-03 | 4:36 | 49.892
2019-11-03 | 4:36 | 49.892
2019-11-03 | 4:36 | 49.893
2019-11-03 | 4:36 | 49.894
2019-11-03 | 4:36 | 49.897
2019-11-03 | 4:36 | 49.9
2019-11-03 | 4:36 | 49.901
2019-11-03 | 4:36 | 49.903
2019-11-03 | 4:36 | 49.904
2019-11-03 | 4:36 | 49.905
2019-11-03 | 4:36 | 49.905
2019-11-03 | 4:36 | 49.905
2019-11-03 | 4:36 | 49.903
2019-11-03 | 4:36 | 49.901
2019-11-03 | 4:36 | 49.899
2019-11-03 | 4:36 | 49.898
2019-11-03 | 4:36 | 49.897
2019-11-03 | 4:36 | 49.896
2019-11-03 | 4:36 | 49.897
2019-11-03 | 4:36 | 49.899
2019-11-03 | 4:36 | 49.899
2019-11-03 | 4:36 | 49.901
2019-11-03 | 4:36 | 49.901
2019-11-03 | 4:36 | 49.902
2019-11-03 | 4:36 | 49.903
2019-11-03 | 4:36 | 49.904
2019-11-03 | 4:36 | 49.906
2019-11-03 | 4:36 | 49.907
2019-11-03 | 4:37 | 49.908
2019-11-03 | 4:37 | 49.909
2019-11-03 | 4:37 | 49.909
2019-11-03 | 4:37 | 49.91
2019-11-03 | 4:37 | 49.909
2019-11-03 | 4:37 | 49.908
2019-11-03 | 4:37 | 49.907
2019-11-03 | 4:37 | 49.907
2019-11-03 | 4:37 | 49.907
2019-11-03 | 4:37 | 49.907
2019-11-03 | 4:37 | 49.907
2019-11-03 | 4:37 | 49.907
2019-11-03 | 4:37 | 49.907
2019-11-03 | 4:37 | 49.905
2019-11-03 | 4:37 | 49.905
2019-11-03 | 4:37 | 49.905
2019-11-03 | 4:37 | 49.905
2019-11-03 | 4:37 | 49.906
2019-11-03 | 4:37 | 49.907
2019-11-03 | 4:37 | 49.907
2019-11-03 | 4:37 | 49.907
2019-11-03 | 4:37 | 49.907
2019-11-03 | 4:37 | 49.908
2019-11-03 | 4:37 | 49.909
2019-11-03 | 4:37 | 49.911
2019-11-03 | 4:37 | 49.912
2019-11-03 | 4:37 | 49.915
2019-11-03 | 4:37 | 49.917
2019-11-03 | 4:37 | 49.92
2019-11-03 | 4:37 | 49.925
2019-11-03 | 4:37 | 49.926
2019-11-03 | 4:37 | 49.926
2019-11-03 | 4:37 | 49.924
2019-11-03 | 4:37 | 49.922
2019-11-03 | 4:37 | 49.92
2019-11-03 | 4:37 | 49.919
2019-11-03 | 4:37 | 49.917
2019-11-03 | 4:37 | 49.916
2019-11-03 | 4:37 | 49.915
2019-11-03 | 4:37 | 49.916
2019-11-03 | 4:37 | 49.917
2019-11-03 | 4:37 | 49.918
2019-11-03 | 4:37 | 49.92
2019-11-03 | 4:37 | 49.922
2019-11-03 | 4:37 | 49.922
2019-11-03 | 4:37 | 49.922
2019-11-03 | 4:37 | 49.921
2019-11-03 | 4:37 | 49.92
2019-11-03 | 4:37 | 49.919
2019-11-03 | 4:37 | 49.917
2019-11-03 | 4:37 | 49.914
2019-11-03 | 4:37 | 49.914
2019-11-03 | 4:37 | 49.914
2019-11-03 | 4:37 | 49.916
2019-11-03 | 4:37 | 49.918
2019-11-03 | 4:37 | 49.919
2019-11-03 | 4:37 | 49.92
2019-11-03 | 4:37 | 49.92
2019-11-03 | 4:37 | 49.92
2019-11-03 | 4:38 | 49.921
2019-11-03 | 4:38 | 49.923
2019-11-03 | 4:38 | 49.922
2019-11-03 | 4:38 | 49.92
2019-11-03 | 4:38 | 49.919
2019-11-03 | 4:38 | 49.918
2019-11-03 | 4:38 | 49.918
2019-11-03 | 4:38 | 49.919
2019-11-03 | 4:38 | 49.92
2019-11-03 | 4:38 | 49.921
2019-11-03 | 4:38 | 49.92
2019-11-03 | 4:38 | 49.92
2019-11-03 | 4:38 | 49.922
2019-11-03 | 4:38 | 49.925
2019-11-03 | 4:38 | 49.925
2019-11-03 | 4:38 | 49.923
2019-11-03 | 4:38 | 49.92
2019-11-03 | 4:38 | 49.918
2019-11-03 | 4:38 | 49.917
2019-11-03 | 4:38 | 49.919
2019-11-03 | 4:38 | 49.922
2019-11-03 | 4:38 | 49.925
2019-11-03 | 4:38 | 49.927
2019-11-03 | 4:38 | 49.928
2019-11-03 | 4:38 | 49.928
2019-11-03 | 4:38 | 49.929
2019-11-03 | 4:38 | 49.929
2019-11-03 | 4:38 | 49.928
2019-11-03 | 4:38 | 49.926
2019-11-03 | 4:38 | 49.924
2019-11-03 | 4:38 | 49.922
2019-11-03 | 4:38 | 49.92
2019-11-03 | 4:38 | 49.919
2019-11-03 | 4:38 | 49.921
2019-11-03 | 4:38 | 49.922
2019-11-03 | 4:38 | 49.923
2019-11-03 | 4:38 | 49.925
2019-11-03 | 4:38 | 49.926
2019-11-03 | 4:38 | 49.928
2019-11-03 | 4:38 | 49.933
2019-11-03 | 4:38 | 49.936
2019-11-03 | 4:38 | 49.939
2019-11-03 | 4:38 | 49.941
2019-11-03 | 4:38 | 49.941
2019-11-03 | 4:38 | 49.941
2019-11-03 | 4:38 | 49.941
2019-11-03 | 4:38 | 49.939
2019-11-03 | 4:38 | 49.937
2019-11-03 | 4:38 | 49.935
2019-11-03 | 4:38 | 49.933
2019-11-03 | 4:38 | 49.931
2019-11-03 | 4:38 | 49.932
2019-11-03 | 4:38 | 49.931
2019-11-03 | 4:38 | 49.93
2019-11-03 | 4:38 | 49.93
2019-11-03 | 4:38 | 49.932
2019-11-03 | 4:38 | 49.935
2019-11-03 | 4:38 | 49.937
2019-11-03 | 4:38 | 49.938
2019-11-03 | 4:38 | 49.94
2019-11-03 | 4:38 | 49.942
2019-11-03 | 4:39 | 49.945
2019-11-03 | 4:39 | 49.948
2019-11-03 | 4:39 | 49.953
2019-11-03 | 4:39 | 49.958
2019-11-03 | 4:39 | 49.959
2019-11-03 | 4:39 | 49.959
2019-11-03 | 4:39 | 49.959
2019-11-03 | 4:39 | 49.958
2019-11-03 | 4:39 | 49.957
2019-11-03 | 4:39 | 49.957
2019-11-03 | 4:39 | 49.957
2019-11-03 | 4:39 | 49.957
2019-11-03 | 4:39 | 49.956
2019-11-03 | 4:39 | 49.956
2019-11-03 | 4:39 | 49.958
2019-11-03 | 4:39 | 49.96
2019-11-03 | 4:39 | 49.962
2019-11-03 | 4:39 | 49.964
2019-11-03 | 4:39 | 49.968
2019-11-03 | 4:39 | 49.972
2019-11-03 | 4:39 | 49.976
2019-11-03 | 4:39 | 49.979
2019-11-03 | 4:39 | 49.981
2019-11-03 | 4:39 | 49.98
2019-11-03 | 4:39 | 49.98
2019-11-03 | 4:39 | 49.981
2019-11-03 | 4:39 | 49.981
2019-11-03 | 4:39 | 49.981
2019-11-03 | 4:39 | 49.98
2019-11-03 | 4:39 | 49.979
2019-11-03 | 4:39 | 49.977
2019-11-03 | 4:39 | 49.975
2019-11-03 | 4:39 | 49.975
2019-11-03 | 4:39 | 49.974
2019-11-03 | 4:39 | 49.974
2019-11-03 | 4:39 | 49.974
2019-11-03 | 4:39 | 49.974
2019-11-03 | 4:39 | 49.974
2019-11-03 | 4:39 | 49.973
2019-11-03 | 4:39 | 49.971
2019-11-03 | 4:39 | 49.971
2019-11-03 | 4:39 | 49.972
2019-11-03 | 4:39 | 49.974
2019-11-03 | 4:39 | 49.975
2019-11-03 | 4:39 | 49.974
2019-11-03 | 4:39 | 49.974
2019-11-03 | 4:39 | 49.975
2019-11-03 | 4:39 | 49.974
2019-11-03 | 4:39 | 49.973
2019-11-03 | 4:39 | 49.97
2019-11-03 | 4:39 | 49.969
2019-11-03 | 4:39 | 49.967
2019-11-03 | 4:39 | 49.965
2019-11-03 | 4:39 | 49.963
2019-11-03 | 4:39 | 49.96
2019-11-03 | 4:39 | 49.958
2019-11-03 | 4:39 | 49.957
2019-11-03 | 4:39 | 49.957
2019-11-03 | 4:39 | 49.96
2019-11-03 | 4:40 | 49.961
2019-11-03 | 4:40 | 49.96
2019-11-03 | 4:40 | 49.959
2019-11-03 | 4:40 | 49.955
2019-11-03 | 4:40 | 49.954
2019-11-03 | 4:40 | 49.951
2019-11-03 | 4:40 | 49.949
2019-11-03 | 4:40 | 49.948
2019-11-03 | 4:40 | 49.945
2019-11-03 | 4:40 | 49.946
2019-11-03 | 4:40 | 49.949
2019-11-03 | 4:40 | 49.952
2019-11-03 | 4:40 | 49.96
2019-11-03 | 4:40 | 49.963
2019-11-03 | 4:40 | 49.968
2019-11-03 | 4:40 | 49.968
2019-11-03 | 4:40 | 49.967
2019-11-03 | 4:40 | 49.966
2019-11-03 | 4:40 | 49.964
2019-11-03 | 4:40 | 49.962
2019-11-03 | 4:40 | 49.958
2019-11-03 | 4:40 | 49.955
2019-11-03 | 4:40 | 49.954
2019-11-03 | 4:40 | 49.952
2019-11-03 | 4:40 | 49.951
2019-11-03 | 4:40 | 49.952
2019-11-03 | 4:40 | 49.952
2019-11-03 | 4:40 | 49.953
2019-11-03 | 4:40 | 49.956
2019-11-03 | 4:40 | 49.96
2019-11-03 | 4:40 | 49.964
2019-11-03 | 4:40 | 49.965
2019-11-03 | 4:40 | 49.965
2019-11-03 | 4:40 | 49.966
2019-11-03 | 4:40 | 49.966
2019-11-03 | 4:40 | 49.967
2019-11-03 | 4:40 | 49.967
2019-11-03 | 4:40 | 49.967
2019-11-03 | 4:40 | 49.964
2019-11-03 | 4:40 | 49.961
2019-11-03 | 4:40 | 49.959
2019-11-03 | 4:40 | 49.958
2019-11-03 | 4:40 | 49.956
2019-11-03 | 4:40 | 49.957
2019-11-03 | 4:40 | 49.958
2019-11-03 | 4:40 | 49.959
2019-11-03 | 4:40 | 49.962
2019-11-03 | 4:40 | 49.965
2019-11-03 | 4:40 | 49.967
2019-11-03 | 4:40 | 49.966
2019-11-03 | 4:40 | 49.968
2019-11-03 | 4:40 | 49.97
2019-11-03 | 4:40 | 49.972
2019-11-03 | 4:40 | 49.974
2019-11-03 | 4:40 | 49.975
2019-11-03 | 4:40 | 49.974
2019-11-03 | 4:40 | 49.972
2019-11-03 | 4:40 | 49.972
2019-11-03 | 4:40 | 49.973
2019-11-03 | 4:40 | 49.974
2019-11-03 | 4:40 | 49.977
2019-11-03 | 4:41 | 49.978
2019-11-03 | 4:41 | 49.979
2019-11-03 | 4:41 | 49.98
2019-11-03 | 4:41 | 49.981
2019-11-03 | 4:41 | 49.983
2019-11-03 | 4:41 | 49.985
2019-11-03 | 4:41 | 49.986
2019-11-03 | 4:41 | 49.986
2019-11-03 | 4:41 | 49.986
2019-11-03 | 4:41 | 49.985
2019-11-03 | 4:41 | 49.984
2019-11-03 | 4:41 | 49.982
2019-11-03 | 4:41 | 49.982
2019-11-03 | 4:41 | 49.981
2019-11-03 | 4:41 | 49.983
2019-11-03 | 4:41 | 49.984
2019-11-03 | 4:41 | 49.986
2019-11-03 | 4:41 | 49.987
2019-11-03 | 4:41 | 49.987
2019-11-03 | 4:41 | 49.986
2019-11-03 | 4:41 | 49.985
2019-11-03 | 4:41 | 49.984
2019-11-03 | 4:41 | 49.985
2019-11-03 | 4:41 | 49.985
2019-11-03 | 4:41 | 49.986
2019-11-03 | 4:41 | 49.986
2019-11-03 | 4:41 | 49.986
2019-11-03 | 4:41 | 49.986
2019-11-03 | 4:41 | 49.986
2019-11-03 | 4:41 | 49.986
2019-11-03 | 4:41 | 49.986
2019-11-03 | 4:41 | 49.986
2019-11-03 | 4:41 | 49.986
2019-11-03 | 4:41 | 49.987
2019-11-03 | 4:41 | 49.988
2019-11-03 | 4:41 | 49.988
2019-11-03 | 4:41 | 49.987
2019-11-03 | 4:41 | 49.985
2019-11-03 | 4:41 | 49.984
2019-11-03 | 4:41 | 49.983
2019-11-03 | 4:41 | 49.981
2019-11-03 | 4:41 | 49.979
2019-11-03 | 4:41 | 49.978
2019-11-03 | 4:41 | 49.977
2019-11-03 | 4:41 | 49.976
2019-11-03 | 4:41 | 49.976
2019-11-03 | 4:41 | 49.976
2019-11-03 | 4:41 | 49.975
2019-11-03 | 4:41 | 49.975
2019-11-03 | 4:41 | 49.976
2019-11-03 | 4:41 | 49.976
2019-11-03 | 4:41 | 49.978
2019-11-03 | 4:41 | 49.978
2019-11-03 | 4:41 | 49.978
2019-11-03 | 4:41 | 49.978
2019-11-03 | 4:41 | 49.978
2019-11-03 | 4:41 | 49.978
2019-11-03 | 4:41 | 49.98
2019-11-03 | 4:41 | 49.982
2019-11-03 | 4:42 | 49.983
2019-11-03 | 4:42 | 49.983
2019-11-03 | 4:42 | 49.984
2019-11-03 | 4:42 | 49.983
2019-11-03 | 4:42 | 49.982
2019-11-03 | 4:42 | 49.981
2019-11-03 | 4:42 | 49.981
2019-11-03 | 4:42 | 49.98
2019-11-03 | 4:42 | 49.978
2019-11-03 | 4:42 | 49.976
2019-11-03 | 4:42 | 49.975
2019-11-03 | 4:42 | 49.977
2019-11-03 | 4:42 | 49.981
2019-11-03 | 4:42 | 49.984
2019-11-03 | 4:42 | 49.988
2019-11-03 | 4:42 | 49.989
2019-11-03 | 4:42 | 49.989
2019-11-03 | 4:42 | 49.988
2019-11-03 | 4:42 | 49.987
2019-11-03 | 4:42 | 49.984
2019-11-03 | 4:42 | 49.981
2019-11-03 | 4:42 | 49.976
2019-11-03 | 4:42 | 49.974
2019-11-03 | 4:42 | 49.972
2019-11-03 | 4:42 | 49.974
2019-11-03 | 4:42 | 49.978
2019-11-03 | 4:42 | 49.98
2019-11-03 | 4:42 | 49.982
2019-11-03 | 4:42 | 49.983
2019-11-03 | 4:42 | 49.984
2019-11-03 | 4:42 | 49.985
2019-11-03 | 4:42 | 49.985
2019-11-03 | 4:42 | 49.984
2019-11-03 | 4:42 | 49.982
2019-11-03 | 4:42 | 49.982
2019-11-03 | 4:42 | 49.98
2019-11-03 | 4:42 | 49.979
2019-11-03 | 4:42 | 49.977
2019-11-03 | 4:42 | 49.976
2019-11-03 | 4:42 | 49.974
2019-11-03 | 4:42 | 49.974
2019-11-03 | 4:42 | 49.973
2019-11-03 | 4:42 | 49.974
2019-11-03 | 4:42 | 49.978
2019-11-03 | 4:42 | 49.979
2019-11-03 | 4:42 | 49.979
2019-11-03 | 4:42 | 49.978
2019-11-03 | 4:42 | 49.977
2019-11-03 | 4:42 | 49.976
2019-11-03 | 4:42 | 49.975
2019-11-03 | 4:42 | 49.971
2019-11-03 | 4:42 | 49.968
2019-11-03 | 4:42 | 49.966
2019-11-03 | 4:42 | 49.965
2019-11-03 | 4:42 | 49.966
2019-11-03 | 4:42 | 49.967
2019-11-03 | 4:42 | 49.967
2019-11-03 | 4:42 | 49.968
2019-11-03 | 4:42 | 49.97
2019-11-03 | 4:42 | 49.972
2019-11-03 | 4:42 | 49.975
2019-11-03 | 4:43 | 49.975
2019-11-03 | 4:43 | 49.976
2019-11-03 | 4:43 | 49.977
2019-11-03 | 4:43 | 49.98
2019-11-03 | 4:43 | 49.984
2019-11-03 | 4:43 | 49.987
2019-11-03 | 4:43 | 49.989
2019-11-03 | 4:43 | 49.991
2019-11-03 | 4:43 | 49.993
2019-11-03 | 4:43 | 49.996
2019-11-03 | 4:43 | 49.998
2019-11-03 | 4:43 | 50
2019-11-03 | 4:43 | 49.999
2019-11-03 | 4:43 | 49.996
2019-11-03 | 4:43 | 49.992
2019-11-03 | 4:43 | 49.99
2019-11-03 | 4:43 | 49.989
2019-11-03 | 4:43 | 49.989
2019-11-03 | 4:43 | 49.99
2019-11-03 | 4:43 | 49.99
2019-11-03 | 4:43 | 49.989
2019-11-03 | 4:43 | 49.99
2019-11-03 | 4:43 | 49.991
2019-11-03 | 4:43 | 49.992
2019-11-03 | 4:43 | 49.994
2019-11-03 | 4:43 | 49.994
2019-11-03 | 4:43 | 49.993
2019-11-03 | 4:43 | 49.994
2019-11-03 | 4:43 | 49.994
2019-11-03 | 4:43 | 49.993
2019-11-03 | 4:43 | 49.991
2019-11-03 | 4:43 | 49.988
2019-11-03 | 4:43 | 49.987
2019-11-03 | 4:43 | 49.986
2019-11-03 | 4:43 | 49.985
2019-11-03 | 4:43 | 49.984
2019-11-03 | 4:43 | 49.984
2019-11-03 | 4:43 | 49.984
2019-11-03 | 4:43 | 49.985
2019-11-03 | 4:43 | 49.985
2019-11-03 | 4:43 | 49.984
2019-11-03 | 4:43 | 49.983
2019-11-03 | 4:43 | 49.984
2019-11-03 | 4:43 | 49.984
2019-11-03 | 4:43 | 49.985
2019-11-03 | 4:43 | 49.984
2019-11-03 | 4:43 | 49.982
2019-11-03 | 4:43 | 49.982
2019-11-03 | 4:43 | 49.98
2019-11-03 | 4:43 | 49.978
2019-11-03 | 4:43 | 49.976
2019-11-03 | 4:43 | 49.976
2019-11-03 | 4:43 | 49.976
2019-11-03 | 4:43 | 49.977
2019-11-03 | 4:43 | 49.978
2019-11-03 | 4:43 | 49.979
2019-11-03 | 4:43 | 49.98
2019-11-03 | 4:43 | 49.98
2019-11-03 | 4:43 | 49.98
2019-11-03 | 4:44 | 49.977
2019-11-03 | 4:44 | 49.974
2019-11-03 | 4:44 | 49.971
2019-11-03 | 4:44 | 49.968
2019-11-03 | 4:44 | 49.966
2019-11-03 | 4:44 | 49.963
2019-11-03 | 4:44 | 49.964
2019-11-03 | 4:44 | 49.965
2019-11-03 | 4:44 | 49.966
2019-11-03 | 4:44 | 49.965
2019-11-03 | 4:44 | 49.967
2019-11-03 | 4:44 | 49.969
2019-11-03 | 4:44 | 49.968
2019-11-03 | 4:44 | 49.969
2019-11-03 | 4:44 | 49.968
2019-11-03 | 4:44 | 49.967
2019-11-03 | 4:44 | 49.964
2019-11-03 | 4:44 | 49.963
2019-11-03 | 4:44 | 49.963
2019-11-03 | 4:44 | 49.964
2019-11-03 | 4:44 | 49.966
2019-11-03 | 4:44 | 49.97
2019-11-03 | 4:44 | 49.971
2019-11-03 | 4:44 | 49.969
2019-11-03 | 4:44 | 49.969
2019-11-03 | 4:44 | 49.968
2019-11-03 | 4:44 | 49.966
2019-11-03 | 4:44 | 49.963
2019-11-03 | 4:44 | 49.959
2019-11-03 | 4:44 | 49.955
2019-11-03 | 4:44 | 49.953
2019-11-03 | 4:44 | 49.955
2019-11-03 | 4:44 | 49.957
2019-11-03 | 4:44 | 49.96
2019-11-03 | 4:44 | 49.963
2019-11-03 | 4:44 | 49.965
2019-11-03 | 4:44 | 49.966
2019-11-03 | 4:44 | 49.966
2019-11-03 | 4:44 | 49.966
2019-11-03 | 4:44 | 49.966
2019-11-03 | 4:44 | 49.963
2019-11-03 | 4:44 | 49.961
2019-11-03 | 4:44 | 49.96
2019-11-03 | 4:44 | 49.959
2019-11-03 | 4:44 | 49.959
2019-11-03 | 4:44 | 49.96
2019-11-03 | 4:44 | 49.961
2019-11-03 | 4:44 | 49.963
2019-11-03 | 4:44 | 49.965
2019-11-03 | 4:44 | 49.967
2019-11-03 | 4:44 | 49.972
2019-11-03 | 4:44 | 49.972
2019-11-03 | 4:44 | 49.972
2019-11-03 | 4:44 | 49.971
2019-11-03 | 4:44 | 49.97
2019-11-03 | 4:44 | 49.97
2019-11-03 | 4:44 | 49.969
2019-11-03 | 4:44 | 49.967
2019-11-03 | 4:44 | 49.963
2019-11-03 | 4:44 | 49.961
2019-11-03 | 4:44 | 49.959
2019-11-03 | 4:45 | 49.958
2019-11-03 | 4:45 | 49.958
2019-11-03 | 4:45 | 49.958
2019-11-03 | 4:45 | 49.959
2019-11-03 | 4:45 | 49.959
2019-11-03 | 4:45 | 49.961
2019-11-03 | 4:45 | 49.963
2019-11-03 | 4:45 | 49.966
2019-11-03 | 4:45 | 49.966
2019-11-03 | 4:45 | 49.967
2019-11-03 | 4:45 | 49.969
2019-11-03 | 4:45 | 49.971
2019-11-03 | 4:45 | 49.973
2019-11-03 | 4:45 | 49.974
2019-11-03 | 4:45 | 49.974
2019-11-03 | 4:45 | 49.974
2019-11-03 | 4:45 | 49.974
2019-11-03 | 4:45 | 49.974
2019-11-03 | 4:45 | 49.974
2019-11-03 | 4:45 | 49.973
2019-11-03 | 4:45 | 49.972
2019-11-03 | 4:45 | 49.972
2019-11-03 | 4:45 | 49.973
2019-11-03 | 4:45 | 49.976
2019-11-03 | 4:45 | 49.979
2019-11-03 | 4:45 | 49.979
2019-11-03 | 4:45 | 49.979
2019-11-03 | 4:45 | 49.977
2019-11-03 | 4:45 | 49.975
2019-11-03 | 4:45 | 49.973
2019-11-03 | 4:45 | 49.971
2019-11-03 | 4:45 | 49.969
2019-11-03 | 4:45 | 49.968
2019-11-03 | 4:45 | 49.967
2019-11-03 | 4:45 | 49.967
2019-11-03 | 4:45 | 49.969
2019-11-03 | 4:45 | 49.969
2019-11-03 | 4:45 | 49.97
2019-11-03 | 4:45 | 49.97
2019-11-03 | 4:45 | 49.97
2019-11-03 | 4:45 | 49.969
2019-11-03 | 4:45 | 49.968
2019-11-03 | 4:45 | 49.967
2019-11-03 | 4:45 | 49.967
2019-11-03 | 4:45 | 49.968
2019-11-03 | 4:45 | 49.971
2019-11-03 | 4:45 | 49.973
2019-11-03 | 4:45 | 49.975
2019-11-03 | 4:45 | 49.975
2019-11-03 | 4:45 | 49.975
2019-11-03 | 4:45 | 49.975
2019-11-03 | 4:45 | 49.974
2019-11-03 | 4:45 | 49.975
2019-11-03 | 4:45 | 49.976
2019-11-03 | 4:45 | 49.974
2019-11-03 | 4:45 | 49.972
2019-11-03 | 4:45 | 49.972
2019-11-03 | 4:45 | 49.972
2019-11-03 | 4:45 | 49.974
2019-11-03 | 4:46 | 49.975
2019-11-03 | 4:46 | 49.977
2019-11-03 | 4:46 | 49.977
2019-11-03 | 4:46 | 49.978
2019-11-03 | 4:46 | 49.977
2019-11-03 | 4:46 | 49.975
2019-11-03 | 4:46 | 49.972
2019-11-03 | 4:46 | 49.969
2019-11-03 | 4:46 | 49.967
2019-11-03 | 4:46 | 49.964
2019-11-03 | 4:46 | 49.962
2019-11-03 | 4:46 | 49.961
2019-11-03 | 4:46 | 49.959
2019-11-03 | 4:46 | 49.959
2019-11-03 | 4:46 | 49.96
2019-11-03 | 4:46 | 49.967
2019-11-03 | 4:46 | 49.976
2019-11-03 | 4:46 | 49.985
2019-11-03 | 4:46 | 49.991
2019-11-03 | 4:46 | 49.995
2019-11-03 | 4:46 | 49.996
2019-11-03 | 4:46 | 49.994
2019-11-03 | 4:46 | 49.992
2019-11-03 | 4:46 | 49.988
2019-11-03 | 4:46 | 49.983
2019-11-03 | 4:46 | 49.979
2019-11-03 | 4:46 | 49.973
2019-11-03 | 4:46 | 49.97
2019-11-03 | 4:46 | 49.968
2019-11-03 | 4:46 | 49.966
2019-11-03 | 4:46 | 49.966
2019-11-03 | 4:46 | 49.968
2019-11-03 | 4:46 | 49.969
2019-11-03 | 4:46 | 49.97
2019-11-03 | 4:46 | 49.969
2019-11-03 | 4:46 | 49.967
2019-11-03 | 4:46 | 49.967
2019-11-03 | 4:46 | 49.965
2019-11-03 | 4:46 | 49.964
2019-11-03 | 4:46 | 49.961
2019-11-03 | 4:46 | 49.958
2019-11-03 | 4:46 | 49.956
2019-11-03 | 4:46 | 49.955
2019-11-03 | 4:46 | 49.959
2019-11-03 | 4:46 | 49.962
2019-11-03 | 4:46 | 49.965
2019-11-03 | 4:46 | 49.967
2019-11-03 | 4:46 | 49.968
2019-11-03 | 4:46 | 49.969
2019-11-03 | 4:46 | 49.971
2019-11-03 | 4:46 | 49.971
2019-11-03 | 4:46 | 49.967
2019-11-03 | 4:46 | 49.965
2019-11-03 | 4:46 | 49.964
2019-11-03 | 4:46 | 49.965
2019-11-03 | 4:46 | 49.967
2019-11-03 | 4:46 | 49.968
2019-11-03 | 4:46 | 49.967
2019-11-03 | 4:46 | 49.967
2019-11-03 | 4:46 | 49.968
2019-11-03 | 4:46 | 49.97
2019-11-03 | 4:47 | 49.973
2019-11-03 | 4:47 | 49.977
2019-11-03 | 4:47 | 49.978
2019-11-03 | 4:47 | 49.979
2019-11-03 | 4:47 | 49.979
2019-11-03 | 4:47 | 49.978
2019-11-03 | 4:47 | 49.978
2019-11-03 | 4:47 | 49.977
2019-11-03 | 4:47 | 49.974
2019-11-03 | 4:47 | 49.971
2019-11-03 | 4:47 | 49.968
2019-11-03 | 4:47 | 49.966
2019-11-03 | 4:47 | 49.965
2019-11-03 | 4:47 | 49.964
2019-11-03 | 4:47 | 49.964
2019-11-03 | 4:47 | 49.964
2019-11-03 | 4:47 | 49.963
2019-11-03 | 4:47 | 49.965
2019-11-03 | 4:47 | 49.966
2019-11-03 | 4:47 | 49.967
2019-11-03 | 4:47 | 49.969
2019-11-03 | 4:47 | 49.972
2019-11-03 | 4:47 | 49.977
2019-11-03 | 4:47 | 49.982
2019-11-03 | 4:47 | 49.985
2019-11-03 | 4:47 | 49.986
2019-11-03 | 4:47 | 49.988
2019-11-03 | 4:47 | 49.992
2019-11-03 | 4:47 | 49.995
2019-11-03 | 4:47 | 49.997
2019-11-03 | 4:47 | 49.983
2019-11-03 | 4:47 | 49.994
2019-11-03 | 4:47 | 49.99
2019-11-03 | 4:47 | 49.986
2019-11-03 | 4:47 | 49.982
2019-11-03 | 4:47 | 49.982
2019-11-03 | 4:47 | 49.984
2019-11-03 | 4:47 | 49.985
2019-11-03 | 4:47 | 49.986
2019-11-03 | 4:47 | 49.987
2019-11-03 | 4:47 | 49.988
2019-11-03 | 4:47 | 49.987
2019-11-03 | 4:47 | 49.987
2019-11-03 | 4:47 | 49.988
2019-11-03 | 4:47 | 49.99
2019-11-03 | 4:47 | 49.991
2019-11-03 | 4:47 | 49.991
2019-11-03 | 4:47 | 49.992
2019-11-03 | 4:47 | 49.993
2019-11-03 | 4:47 | 49.994
2019-11-03 | 4:47 | 49.994
2019-11-03 | 4:47 | 49.993
2019-11-03 | 4:47 | 49.992
2019-11-03 | 4:47 | 49.992
2019-11-03 | 4:47 | 49.991
2019-11-03 | 4:47 | 49.991
2019-11-03 | 4:47 | 49.991
2019-11-03 | 4:47 | 49.992
2019-11-03 | 4:47 | 49.994
2019-11-03 | 4:48 | 49.994
2019-11-03 | 4:48 | 49.993
2019-11-03 | 4:48 | 49.991
2019-11-03 | 4:48 | 49.989
2019-11-03 | 4:48 | 49.987
2019-11-03 | 4:48 | 49.986
2019-11-03 | 4:48 | 49.988
2019-11-03 | 4:48 | 49.99
2019-11-03 | 4:48 | 49.992
2019-11-03 | 4:48 | 49.992
2019-11-03 | 4:48 | 49.994
2019-11-03 | 4:48 | 49.993
2019-11-03 | 4:48 | 49.992
2019-11-03 | 4:48 | 49.991
2019-11-03 | 4:48 | 49.989
2019-11-03 | 4:48 | 49.989
2019-11-03 | 4:48 | 49.989
2019-11-03 | 4:48 | 49.989
2019-11-03 | 4:48 | 49.988
2019-11-03 | 4:48 | 49.985
2019-11-03 | 4:48 | 49.984
2019-11-03 | 4:48 | 49.983
2019-11-03 | 4:48 | 49.983
2019-11-03 | 4:48 | 49.984
2019-11-03 | 4:48 | 49.987
2019-11-03 | 4:48 | 49.989
2019-11-03 | 4:48 | 49.991
2019-11-03 | 4:48 | 49.993
2019-11-03 | 4:48 | 49.995
2019-11-03 | 4:48 | 49.995
2019-11-03 | 4:48 | 49.994
2019-11-03 | 4:48 | 49.994
2019-11-03 | 4:48 | 49.991
2019-11-03 | 4:48 | 49.988
2019-11-03 | 4:48 | 49.984
2019-11-03 | 4:48 | 49.983
2019-11-03 | 4:48 | 49.983
2019-11-03 | 4:48 | 49.986
2019-11-03 | 4:48 | 49.989
2019-11-03 | 4:48 | 49.993
2019-11-03 | 4:48 | 49.994
2019-11-03 | 4:48 | 49.993
2019-11-03 | 4:48 | 49.993
2019-11-03 | 4:48 | 49.993
2019-11-03 | 4:48 | 49.992
2019-11-03 | 4:48 | 49.99
2019-11-03 | 4:48 | 49.988
2019-11-03 | 4:48 | 49.983
2019-11-03 | 4:48 | 49.981
2019-11-03 | 4:48 | 49.981
2019-11-03 | 4:48 | 49.983
2019-11-03 | 4:48 | 49.986
2019-11-03 | 4:48 | 49.987
2019-11-03 | 4:48 | 49.987
2019-11-03 | 4:48 | 49.986
2019-11-03 | 4:48 | 49.986
2019-11-03 | 4:48 | 49.985
2019-11-03 | 4:48 | 49.984
2019-11-03 | 4:48 | 49.981
2019-11-03 | 4:48 | 49.979
2019-11-03 | 4:48 | 49.978
2019-11-03 | 4:49 | 49.979
2019-11-03 | 4:49 | 49.981
2019-11-03 | 4:49 | 49.981
2019-11-03 | 4:49 | 49.982
2019-11-03 | 4:49 | 49.982
2019-11-03 | 4:49 | 49.981
2019-11-03 | 4:49 | 49.982
2019-11-03 | 4:49 | 49.985
2019-11-03 | 4:49 | 49.988
2019-11-03 | 4:49 | 49.988
2019-11-03 | 4:49 | 49.987
2019-11-03 | 4:49 | 49.987
2019-11-03 | 4:49 | 49.984
2019-11-03 | 4:49 | 49.982
2019-11-03 | 4:49 | 49.979
2019-11-03 | 4:49 | 49.974
2019-11-03 | 4:49 | 49.971
2019-11-03 | 4:49 | 49.97
2019-11-03 | 4:49 | 49.971
2019-11-03 | 4:49 | 49.972
2019-11-03 | 4:49 | 49.973
2019-11-03 | 4:49 | 49.975
2019-11-03 | 4:49 | 49.976
2019-11-03 | 4:49 | 49.979
2019-11-03 | 4:49 | 49.982
2019-11-03 | 4:49 | 49.985
2019-11-03 | 4:49 | 49.986
2019-11-03 | 4:49 | 49.988
2019-11-03 | 4:49 | 49.99
2019-11-03 | 4:49 | 49.993
2019-11-03 | 4:49 | 49.994
2019-11-03 | 4:49 | 49.993
2019-11-03 | 4:49 | 49.994
2019-11-03 | 4:49 | 49.992
2019-11-03 | 4:49 | 49.991
2019-11-03 | 4:49 | 49.992
2019-11-03 | 4:49 | 49.994
2019-11-03 | 4:49 | 49.996
2019-11-03 | 4:49 | 49.998
2019-11-03 | 4:49 | 50
2019-11-03 | 4:49 | 50.002
2019-11-03 | 4:49 | 50.003
2019-11-03 | 4:49 | 50.006
2019-11-03 | 4:49 | 50.008
2019-11-03 | 4:49 | 50.008
2019-11-03 | 4:49 | 50.006
2019-11-03 | 4:49 | 50.006
2019-11-03 | 4:49 | 50.006
2019-11-03 | 4:49 | 50.006
2019-11-03 | 4:49 | 50.005
2019-11-03 | 4:49 | 50.006
2019-11-03 | 4:49 | 50.009
2019-11-03 | 4:49 | 50.01
2019-11-03 | 4:49 | 50.014
2019-11-03 | 4:49 | 50.015
2019-11-03 | 4:49 | 50.016
2019-11-03 | 4:49 | 50.015
2019-11-03 | 4:49 | 50.016
2019-11-03 | 4:49 | 50.015
2019-11-03 | 4:50 | 50.015
2019-11-03 | 4:50 | 50.013
2019-11-03 | 4:50 | 50.011
2019-11-03 | 4:50 | 50.009
2019-11-03 | 4:50 | 50.008
2019-11-03 | 4:50 | 50.006
2019-11-03 | 4:50 | 50.005
2019-11-03 | 4:50 | 50.005
2019-11-03 | 4:50 | 50.004
2019-11-03 | 4:50 | 50.002
2019-11-03 | 4:50 | 50
2019-11-03 | 4:50 | 49.997
2019-11-03 | 4:50 | 49.994
2019-11-03 | 4:50 | 49.992
2019-11-03 | 4:50 | 49.991
2019-11-03 | 4:50 | 49.991
2019-11-03 | 4:50 | 49.993
2019-11-03 | 4:50 | 49.995
2019-11-03 | 4:50 | 49.995
2019-11-03 | 4:50 | 49.995
2019-11-03 | 4:50 | 49.993
2019-11-03 | 4:50 | 49.99
2019-11-03 | 4:50 | 49.988
2019-11-03 | 4:50 | 49.985
2019-11-03 | 4:50 | 49.985
2019-11-03 | 4:50 | 49.986
2019-11-03 | 4:50 | 49.987
2019-11-03 | 4:50 | 49.988
2019-11-03 | 4:50 | 49.988
2019-11-03 | 4:50 | 49.987

## Event 20191106-1
In UTC
Date | Time | Freq
2019-11-06 | 13:49 | 50.06
2019-11-06 | 13:49 | 50.059
2019-11-06 | 13:49 | 50.058
2019-11-06 | 13:49 | 50.057
2019-11-06 | 13:49 | 50.056
2019-11-06 | 13:49 | 50.056
2019-11-06 | 13:49 | 50.054
2019-11-06 | 13:49 | 50.053
2019-11-06 | 13:49 | 50.051
2019-11-06 | 13:49 | 50.05
2019-11-06 | 13:49 | 50.048
2019-11-06 | 13:49 | 50.048
2019-11-06 | 13:49 | 50.047
2019-11-06 | 13:49 | 50.048
2019-11-06 | 13:49 | 50.046
2019-11-06 | 13:49 | 50.045
2019-11-06 | 13:49 | 50.044
2019-11-06 | 13:49 | 50.043
2019-11-06 | 13:49 | 50.042
2019-11-06 | 13:49 | 50.04
2019-11-06 | 13:49 | 50.038
2019-11-06 | 13:49 | 50.039
2019-11-06 | 13:49 | 50.039
2019-11-06 | 13:49 | 50.04
2019-11-06 | 13:49 | 50.042
2019-11-06 | 13:49 | 50.045
2019-11-06 | 13:49 | 50.048
2019-11-06 | 13:49 | 50.055
2019-11-06 | 13:49 | 50.06
2019-11-06 | 13:49 | 50.065
2019-11-06 | 13:50 | 50.069
2019-11-06 | 13:50 | 50.072
2019-11-06 | 13:50 | 50.075
2019-11-06 | 13:50 | 50.078
2019-11-06 | 13:50 | 50.08
2019-11-06 | 13:50 | 50.081
2019-11-06 | 13:50 | 50.081
2019-11-06 | 13:50 | 50.081
2019-11-06 | 13:50 | 50.081
2019-11-06 | 13:50 | 50.081
2019-11-06 | 13:50 | 50.082
2019-11-06 | 13:50 | 50.082
2019-11-06 | 13:50 | 50.082
2019-11-06 | 13:50 | 50.082
2019-11-06 | 13:50 | 50.082
2019-11-06 | 13:50 | 50.081
2019-11-06 | 13:50 | 50.08
2019-11-06 | 13:50 | 50.078
2019-11-06 | 13:50 | 50.074
2019-11-06 | 13:50 | 50.071
2019-11-06 | 13:50 | 50.066
2019-11-06 | 13:50 | 50.06
2019-11-06 | 13:50 | 50.054
2019-11-06 | 13:50 | 50.048
2019-11-06 | 13:50 | 50.042
2019-11-06 | 13:50 | 50.04
2019-11-06 | 13:50 | 50.038
2019-11-06 | 13:50 | 50.035
2019-11-06 | 13:50 | 50.034
2019-11-06 | 13:50 | 50.034
2019-11-06 | 13:50 | 50.034
2019-11-06 | 13:50 | 50.033
2019-11-06 | 13:50 | 50.033
2019-11-06 | 13:50 | 50.035
2019-11-06 | 13:50 | 50.037
2019-11-06 | 13:50 | 50.039
2019-11-06 | 13:50 | 50.042
2019-11-06 | 13:50 | 50.046
2019-11-06 | 13:50 | 50.049
2019-11-06 | 13:50 | 50.052
2019-11-06 | 13:50 | 50.044
2019-11-06 | 13:50 | 50.033
2019-11-06 | 13:50 | 50.021
2019-11-06 | 13:50 | 50.01
2019-11-06 | 13:50 | 50
2019-11-06 | 13:50 | 49.992
2019-11-06 | 13:50 | 49.983
2019-11-06 | 13:50 | 49.977
2019-11-06 | 13:50 | 49.969
2019-11-06 | 13:50 | 49.966
2019-11-06 | 13:50 | 49.964
2019-11-06 | 13:50 | 49.964
2019-11-06 | 13:50 | 49.964
2019-11-06 | 13:50 | 49.964
2019-11-06 | 13:50 | 49.966
2019-11-06 | 13:50 | 49.967
2019-11-06 | 13:50 | 49.969
2019-11-06 | 13:50 | 49.972
2019-11-06 | 13:50 | 49.976
2019-11-06 | 13:50 | 49.978
2019-11-06 | 13:50 | 49.981
2019-11-06 | 13:51 | 49.982
2019-11-06 | 13:51 | 49.983
2019-11-06 | 13:51 | 49.985
2019-11-06 | 13:51 | 49.986
2019-11-06 | 13:51 | 49.987
2019-11-06 | 13:51 | 49.987
2019-11-06 | 13:51 | 49.989
2019-11-06 | 13:51 | 49.985
2019-11-06 | 13:51 | 49.986
2019-11-06 | 13:51 | 49.986
2019-11-06 | 13:51 | 49.988
2019-11-06 | 13:51 | 49.989
2019-11-06 | 13:51 | 49.99
2019-11-06 | 13:51 | 49.991
2019-11-06 | 13:51 | 49.992
2019-11-06 | 13:51 | 49.991
2019-11-06 | 13:51 | 49.99
2019-11-06 | 13:51 | 49.988
2019-11-06 | 13:51 | 49.986
2019-11-06 | 13:51 | 49.987
2019-11-06 | 13:51 | 49.986
2019-11-06 | 13:51 | 49.987
2019-11-06 | 13:51 | 49.987
2019-11-06 | 13:51 | 49.988
2019-11-06 | 13:51 | 49.988
2019-11-06 | 13:51 | 49.986
2019-11-06 | 13:51 | 49.985
2019-11-06 | 13:51 | 49.982
2019-11-06 | 13:51 | 49.98
2019-11-06 | 13:51 | 49.976
2019-11-06 | 13:51 | 49.974
2019-11-06 | 13:51 | 49.972
2019-11-06 | 13:51 | 49.971
2019-11-06 | 13:51 | 49.971
2019-11-06 | 13:51 | 49.97
2019-11-06 | 13:51 | 49.968
2019-11-06 | 13:51 | 49.966
2019-11-06 | 13:51 | 49.965
2019-11-06 | 13:51 | 49.966
2019-11-06 | 13:51 | 49.968
2019-11-06 | 13:51 | 49.97
2019-11-06 | 13:51 | 49.97
2019-11-06 | 13:51 | 49.97
2019-11-06 | 13:51 | 49.971
2019-11-06 | 13:51 | 49.971
2019-11-06 | 13:51 | 49.97
2019-11-06 | 13:51 | 49.968
2019-11-06 | 13:51 | 49.968
2019-11-06 | 13:51 | 49.969
2019-11-06 | 13:51 | 49.969
2019-11-06 | 13:51 | 49.97
2019-11-06 | 13:51 | 49.969
2019-11-06 | 13:51 | 49.97
2019-11-06 | 13:51 | 49.97
2019-11-06 | 13:51 | 49.97
2019-11-06 | 13:51 | 49.969
2019-11-06 | 13:51 | 49.968
2019-11-06 | 13:51 | 49.967
2019-11-06 | 13:51 | 49.966
2019-11-06 | 13:52 | 49.966
2019-11-06 | 13:52 | 49.964
2019-11-06 | 13:52 | 49.964
2019-11-06 | 13:52 | 49.963
2019-11-06 | 13:52 | 49.962
2019-11-06 | 13:52 | 49.964
2019-11-06 | 13:52 | 49.965
2019-11-06 | 13:52 | 49.966
2019-11-06 | 13:52 | 49.967
2019-11-06 | 13:52 | 49.968
2019-11-06 | 13:52 | 49.968
2019-11-06 | 13:52 | 49.968
2019-11-06 | 13:52 | 49.969
2019-11-06 | 13:52 | 49.97
2019-11-06 | 13:52 | 49.97
2019-11-06 | 13:52 | 49.969
2019-11-06 | 13:52 | 49.967
2019-11-06 | 13:52 | 49.966
2019-11-06 | 13:52 | 49.964
2019-11-06 | 13:52 | 49.966
2019-11-06 | 13:52 | 49.966
2019-11-06 | 13:52 | 49.967
2019-11-06 | 13:52 | 49.967
2019-11-06 | 13:52 | 49.967
2019-11-06 | 13:52 | 49.965
2019-11-06 | 13:52 | 49.96
2019-11-06 | 13:52 | 49.959
2019-11-06 | 13:52 | 49.956
2019-11-06 | 13:52 | 49.954
2019-11-06 | 13:52 | 49.951
2019-11-06 | 13:52 | 49.948
2019-11-06 | 13:52 | 49.945
2019-11-06 | 13:52 | 49.943
2019-11-06 | 13:52 | 49.941
2019-11-06 | 13:52 | 49.94
2019-11-06 | 13:52 | 49.937
2019-11-06 | 13:52 | 49.936
2019-11-06 | 13:52 | 49.933
2019-11-06 | 13:52 | 49.931
2019-11-06 | 13:52 | 49.93
2019-11-06 | 13:52 | 49.93
2019-11-06 | 13:52 | 49.93
2019-11-06 | 13:52 | 49.931
2019-11-06 | 13:52 | 49.932
2019-11-06 | 13:52 | 49.933
2019-11-06 | 13:52 | 49.935
2019-11-06 | 13:52 | 49.935
2019-11-06 | 13:52 | 49.935
2019-11-06 | 13:52 | 49.935
2019-11-06 | 13:52 | 49.934
2019-11-06 | 13:52 | 49.933
2019-11-06 | 13:52 | 49.932
2019-11-06 | 13:52 | 49.93
2019-11-06 | 13:52 | 49.928
2019-11-06 | 13:52 | 49.926
2019-11-06 | 13:52 | 49.925
2019-11-06 | 13:52 | 49.923
2019-11-06 | 13:52 | 49.922
2019-11-06 | 13:52 | 49.921
2019-11-06 | 13:52 | 49.919
2019-11-06 | 13:52 | 49.919
2019-11-06 | 13:53 | 49.917
2019-11-06 | 13:53 | 49.917
2019-11-06 | 13:53 | 49.917
2019-11-06 | 13:53 | 49.917
2019-11-06 | 13:53 | 49.917
2019-11-06 | 13:53 | 49.919
2019-11-06 | 13:53 | 49.922
2019-11-06 | 13:53 | 49.924
2019-11-06 | 13:53 | 49.928
2019-11-06 | 13:53 | 49.93
2019-11-06 | 13:53 | 49.934
2019-11-06 | 13:53 | 49.937
2019-11-06 | 13:53 | 49.94
2019-11-06 | 13:53 | 49.945
2019-11-06 | 13:53 | 49.947
2019-11-06 | 13:53 | 49.95
2019-11-06 | 13:53 | 49.952
2019-11-06 | 13:53 | 49.954
2019-11-06 | 13:53 | 49.953
2019-11-06 | 13:53 | 49.952
2019-11-06 | 13:53 | 49.95
2019-11-06 | 13:53 | 49.948
2019-11-06 | 13:53 | 49.946
2019-11-06 | 13:53 | 49.944
2019-11-06 | 13:53 | 49.943
2019-11-06 | 13:53 | 49.942
2019-11-06 | 13:53 | 49.941
2019-11-06 | 13:53 | 49.942
2019-11-06 | 13:53 | 49.942
2019-11-06 | 13:53 | 49.941
2019-11-06 | 13:53 | 49.941
2019-11-06 | 13:53 | 49.94
2019-11-06 | 13:53 | 49.939
2019-11-06 | 13:53 | 49.937
2019-11-06 | 13:53 | 49.934
2019-11-06 | 13:53 | 49.928
2019-11-06 | 13:53 | 49.922
2019-11-06 | 13:53 | 49.914
2019-11-06 | 13:53 | 49.905
2019-11-06 | 13:53 | 49.895
2019-11-06 | 13:53 | 49.884
2019-11-06 | 13:53 | 49.877
2019-11-06 | 13:53 | 49.868
2019-11-06 | 13:53 | 49.863
2019-11-06 | 13:53 | 49.856
2019-11-06 | 13:53 | 49.853
2019-11-06 | 13:53 | 49.85
2019-11-06 | 13:53 | 49.849
2019-11-06 | 13:53 | 49.848
2019-11-06 | 13:53 | 49.848
2019-11-06 | 13:53 | 49.848
2019-11-06 | 13:53 | 49.847
2019-11-06 | 13:53 | 49.848
2019-11-06 | 13:53 | 49.85
2019-11-06 | 13:53 | 49.851
2019-11-06 | 13:53 | 49.854
2019-11-06 | 13:53 | 49.857
2019-11-06 | 13:53 | 49.859
2019-11-06 | 13:53 | 49.859
2019-11-06 | 13:54 | 49.859
2019-11-06 | 13:54 | 49.86
2019-11-06 | 13:54 | 49.861
2019-11-06 | 13:54 | 49.861
2019-11-06 | 13:54 | 49.862
2019-11-06 | 13:54 | 49.863
2019-11-06 | 13:54 | 49.865
2019-11-06 | 13:54 | 49.866
2019-11-06 | 13:54 | 49.868
2019-11-06 | 13:54 | 49.869
2019-11-06 | 13:54 | 49.867
2019-11-06 | 13:54 | 49.866
2019-11-06 | 13:54 | 49.865
2019-11-06 | 13:54 | 49.861
2019-11-06 | 13:54 | 49.859
2019-11-06 | 13:54 | 49.857
2019-11-06 | 13:54 | 49.857
2019-11-06 | 13:54 | 49.858
2019-11-06 | 13:54 | 49.859
2019-11-06 | 13:54 | 49.861
2019-11-06 | 13:54 | 49.863
2019-11-06 | 13:54 | 49.865
2019-11-06 | 13:54 | 49.868
2019-11-06 | 13:54 | 49.872
2019-11-06 | 13:54 | 49.875
2019-11-06 | 13:54 | 49.876
2019-11-06 | 13:54 | 49.878
2019-11-06 | 13:54 | 49.881
2019-11-06 | 13:54 | 49.882
2019-11-06 | 13:54 | 49.884
2019-11-06 | 13:54 | 49.885
2019-11-06 | 13:54 | 49.887
2019-11-06 | 13:54 | 49.89
2019-11-06 | 13:54 | 49.893
2019-11-06 | 13:54 | 49.896
2019-11-06 | 13:54 | 49.897
2019-11-06 | 13:54 | 49.895
2019-11-06 | 13:54 | 49.895
2019-11-06 | 13:54 | 49.895
2019-11-06 | 13:54 | 49.894
2019-11-06 | 13:54 | 49.894
2019-11-06 | 13:54 | 49.895
2019-11-06 | 13:54 | 49.898
2019-11-06 | 13:54 | 49.902
2019-11-06 | 13:54 | 49.906
2019-11-06 | 13:54 | 49.911
2019-11-06 | 13:54 | 49.916
2019-11-06 | 13:54 | 49.923
2019-11-06 | 13:54 | 49.931
2019-11-06 | 13:54 | 49.937
2019-11-06 | 13:54 | 49.942
2019-11-06 | 13:54 | 49.944
2019-11-06 | 13:54 | 49.947
2019-11-06 | 13:54 | 49.949
2019-11-06 | 13:54 | 49.951
2019-11-06 | 13:54 | 49.953
2019-11-06 | 13:54 | 49.955
2019-11-06 | 13:54 | 49.956
2019-11-06 | 13:54 | 49.956
2019-11-06 | 13:54 | 49.955
2019-11-06 | 13:54 | 49.954
2019-11-06 | 13:55 | 49.955
2019-11-06 | 13:55 | 49.956
2019-11-06 | 13:55 | 49.957
2019-11-06 | 13:55 | 49.959
2019-11-06 | 13:55 | 49.959
2019-11-06 | 13:55 | 49.96
2019-11-06 | 13:55 | 49.961
2019-11-06 | 13:55 | 49.962
2019-11-06 | 13:55 | 49.963
2019-11-06 | 13:55 | 49.964
2019-11-06 | 13:55 | 49.967
2019-11-06 | 13:55 | 49.97
2019-11-06 | 13:55 | 49.973
2019-11-06 | 13:55 | 49.976
2019-11-06 | 13:55 | 49.978
2019-11-06 | 13:55 | 49.98
2019-11-06 | 13:55 | 49.98
2019-11-06 | 13:55 | 49.982
2019-11-06 | 13:55 | 49.981
2019-11-06 | 13:55 | 49.981
2019-11-06 | 13:55 | 49.979
2019-11-06 | 13:55 | 49.978
2019-11-06 | 13:55 | 49.979
2019-11-06 | 13:55 | 49.978
2019-11-06 | 13:55 | 49.978
2019-11-06 | 13:55 | 49.977
2019-11-06 | 13:55 | 49.975
2019-11-06 | 13:55 | 49.973
2019-11-06 | 13:55 | 49.971
2019-11-06 | 13:55 | 49.969
2019-11-06 | 13:55 | 49.966
2019-11-06 | 13:55 | 49.963
2019-11-06 | 13:55 | 49.961
2019-11-06 | 13:55 | 49.96
2019-11-06 | 13:55 | 49.957
2019-11-06 | 13:55 | 49.957
2019-11-06 | 13:55 | 49.956
2019-11-06 | 13:55 | 49.956
2019-11-06 | 13:55 | 49.957
2019-11-06 | 13:55 | 49.958
2019-11-06 | 13:55 | 49.96
2019-11-06 | 13:55 | 49.962
2019-11-06 | 13:55 | 49.962
2019-11-06 | 13:55 | 49.964
2019-11-06 | 13:55 | 49.966
2019-11-06 | 13:55 | 49.97
2019-11-06 | 13:55 | 49.973
2019-11-06 | 13:55 | 49.976
2019-11-06 | 13:55 | 49.981
2019-11-06 | 13:55 | 49.986
2019-11-06 | 13:55 | 49.992
2019-11-06 | 13:55 | 49.998
2019-11-06 | 13:55 | 50.005
2019-11-06 | 13:55 | 50.01
2019-11-06 | 13:55 | 50.014
2019-11-06 | 13:55 | 50.014
2019-11-06 | 13:55 | 50.012
2019-11-06 | 13:55 | 50.014
2019-11-06 | 13:55 | 50.016
2019-11-06 | 13:56 | 50.021
2019-11-06 | 13:56 | 50.023
2019-11-06 | 13:56 | 50.026
2019-11-06 | 13:56 | 50.029
2019-11-06 | 13:56 | 50.032
2019-11-06 | 13:56 | 50.034
2019-11-06 | 13:56 | 50.036
2019-11-06 | 13:56 | 50.037
2019-11-06 | 13:56 | 50.035
2019-11-06 | 13:56 | 50.035
2019-11-06 | 13:56 | 50.034
2019-11-06 | 13:56 | 50.031
2019-11-06 | 13:56 | 50.026
2019-11-06 | 13:56 | 50.019
2019-11-06 | 13:56 | 50.009
2019-11-06 | 13:56 | 49.999
2019-11-06 | 13:56 | 49.989
2019-11-06 | 13:56 | 49.979
2019-11-06 | 13:56 | 49.967
2019-11-06 | 13:56 | 49.954
2019-11-06 | 13:56 | 49.944
2019-11-06 | 13:56 | 49.935
2019-11-06 | 13:56 | 49.928
2019-11-06 | 13:56 | 49.922
2019-11-06 | 13:56 | 49.918
2019-11-06 | 13:56 | 49.916
2019-11-06 | 13:56 | 49.915
2019-11-06 | 13:56 | 49.914
2019-11-06 | 13:56 | 49.914
2019-11-06 | 13:56 | 49.912

## Event 20191114-1
In UTC
Date | Time | Freq
2019-11-14 | 5:16 | 50.056
2019-11-14 | 5:16 | 50.057
2019-11-14 | 5:16 | 50.057
2019-11-14 | 5:16 | 50.056
2019-11-14 | 5:16 | 50.056
2019-11-14 | 5:16 | 50.056
2019-11-14 | 5:16 | 50.056
2019-11-14 | 5:16 | 50.054
2019-11-14 | 5:16 | 50.053
2019-11-14 | 5:16 | 50.051
2019-11-14 | 5:16 | 50.05
2019-11-14 | 5:16 | 50.049
2019-11-14 | 5:16 | 50.051
2019-11-14 | 5:16 | 50.055
2019-11-14 | 5:16 | 50.061
2019-11-14 | 5:16 | 50.064
2019-11-14 | 5:16 | 50.068
2019-11-14 | 5:16 | 50.07
2019-11-14 | 5:16 | 50.072
2019-11-14 | 5:16 | 50.073
2019-11-14 | 5:16 | 50.072
2019-11-14 | 5:16 | 50.071
2019-11-14 | 5:16 | 50.066
2019-11-14 | 5:16 | 50.059
2019-11-14 | 5:16 | 50.056
2019-11-14 | 5:16 | 50.052
2019-11-14 | 5:16 | 50.049
2019-11-14 | 5:16 | 50.046
2019-11-14 | 5:16 | 50.046
2019-11-14 | 5:16 | 50.05
2019-11-14 | 5:17 | 50.053
2019-11-14 | 5:17 | 50.053
2019-11-14 | 5:17 | 50.055
2019-11-14 | 5:17 | 50.058
2019-11-14 | 5:17 | 50.06
2019-11-14 | 5:17 | 50.064
2019-11-14 | 5:17 | 50.063
2019-11-14 | 5:17 | 50.062
2019-11-14 | 5:17 | 50.062
2019-11-14 | 5:17 | 50.06
2019-11-14 | 5:17 | 50.058
2019-11-14 | 5:17 | 50.057
2019-11-14 | 5:17 | 50.057
2019-11-14 | 5:17 | 50.056
2019-11-14 | 5:17 | 50.055
2019-11-14 | 5:17 | 50.054
2019-11-14 | 5:17 | 50.057
2019-11-14 | 5:17 | 50.057
2019-11-14 | 5:17 | 50.059
2019-11-14 | 5:17 | 50.061
2019-11-14 | 5:17 | 50.062
2019-11-14 | 5:17 | 50.063
2019-11-14 | 5:17 | 50.065
2019-11-14 | 5:17 | 50.067
2019-11-14 | 5:17 | 50.067
2019-11-14 | 5:17 | 50.068
2019-11-14 | 5:17 | 50.07
2019-11-14 | 5:17 | 50.072
2019-11-14 | 5:17 | 50.074
2019-11-14 | 5:17 | 50.073
2019-11-14 | 5:17 | 50.073
2019-11-14 | 5:17 | 50.071
2019-11-14 | 5:17 | 50.071
2019-11-14 | 5:17 | 50.07
2019-11-14 | 5:17 | 50.069
2019-11-14 | 5:17 | 50.068
2019-11-14 | 5:17 | 50.069
2019-11-14 | 5:17 | 50.069
2019-11-14 | 5:17 | 50.069
2019-11-14 | 5:17 | 50.07
2019-11-14 | 5:17 | 50.073
2019-11-14 | 5:17 | 50.073
2019-11-14 | 5:17 | 50.076
2019-11-14 | 5:17 | 50.079
2019-11-14 | 5:17 | 50.08
2019-11-14 | 5:17 | 50.081
2019-11-14 | 5:17 | 50.082
2019-11-14 | 5:17 | 50.084
2019-11-14 | 5:17 | 50.084
2019-11-14 | 5:17 | 50.084
2019-11-14 | 5:17 | 50.085
2019-11-14 | 5:17 | 50.085
2019-11-14 | 5:17 | 50.086
2019-11-14 | 5:17 | 50.086
2019-11-14 | 5:17 | 50.087
2019-11-14 | 5:17 | 50.084
2019-11-14 | 5:17 | 50.086
2019-11-14 | 5:17 | 50.086
2019-11-14 | 5:17 | 50.083
2019-11-14 | 5:17 | 50.081
2019-11-14 | 5:18 | 50.081
2019-11-14 | 5:18 | 50.037
2019-11-14 | 5:18 | 49.988
2019-11-14 | 5:18 | 49.941
2019-11-14 | 5:18 | 49.904
2019-11-14 | 5:18 | 49.876
2019-11-14 | 5:18 | 49.858
2019-11-14 | 5:18 | 49.852
2019-11-14 | 5:18 | 49.849
2019-11-14 | 5:18 | 49.848
2019-11-14 | 5:18 | 49.852
2019-11-14 | 5:18 | 49.854
2019-11-14 | 5:18 | 49.856
2019-11-14 | 5:18 | 49.858
2019-11-14 | 5:18 | 49.861
2019-11-14 | 5:18 | 49.863
2019-11-14 | 5:18 | 49.865
2019-11-14 | 5:18 | 49.866
2019-11-14 | 5:18 | 49.867
2019-11-14 | 5:18 | 49.866
2019-11-14 | 5:18 | 49.865
2019-11-14 | 5:18 | 49.864
2019-11-14 | 5:18 | 49.865
2019-11-14 | 5:18 | 49.866
2019-11-14 | 5:18 | 49.867
2019-11-14 | 5:18 | 49.868
2019-11-14 | 5:18 | 49.868
2019-11-14 | 5:18 | 49.868
2019-11-14 | 5:18 | 49.87
2019-11-14 | 5:18 | 49.867
2019-11-14 | 5:18 | 49.868
2019-11-14 | 5:18 | 49.867
2019-11-14 | 5:18 | 49.868
2019-11-14 | 5:18 | 49.866
2019-11-14 | 5:18 | 49.865
2019-11-14 | 5:18 | 49.865
2019-11-14 | 5:18 | 49.866
2019-11-14 | 5:18 | 49.864
2019-11-14 | 5:18 | 49.864
2019-11-14 | 5:18 | 49.863
2019-11-14 | 5:18 | 49.863
2019-11-14 | 5:18 | 49.863
2019-11-14 | 5:18 | 49.863
2019-11-14 | 5:18 | 49.865
2019-11-14 | 5:18 | 49.867
2019-11-14 | 5:18 | 49.868
2019-11-14 | 5:18 | 49.871
2019-11-14 | 5:18 | 49.871
2019-11-14 | 5:18 | 49.873
2019-11-14 | 5:18 | 49.874
2019-11-14 | 5:18 | 49.873
2019-11-14 | 5:18 | 49.873
2019-11-14 | 5:18 | 49.87
2019-11-14 | 5:18 | 49.87
2019-11-14 | 5:18 | 49.869
2019-11-14 | 5:18 | 49.869
2019-11-14 | 5:18 | 49.869
2019-11-14 | 5:18 | 49.871
2019-11-14 | 5:18 | 49.873
2019-11-14 | 5:18 | 49.876
2019-11-14 | 5:18 | 49.877
2019-11-14 | 5:19 | 49.878
2019-11-14 | 5:19 | 49.878
2019-11-14 | 5:19 | 49.878
2019-11-14 | 5:19 | 49.877
2019-11-14 | 5:19 | 49.876
2019-11-14 | 5:19 | 49.871
2019-11-14 | 5:19 | 49.87
2019-11-14 | 5:19 | 49.869
2019-11-14 | 5:19 | 49.87
2019-11-14 | 5:19 | 49.872
2019-11-14 | 5:19 | 49.874
2019-11-14 | 5:19 | 49.88
2019-11-14 | 5:19 | 49.882
2019-11-14 | 5:19 | 49.883
2019-11-14 | 5:19 | 49.883
2019-11-14 | 5:19 | 49.886
2019-11-14 | 5:19 | 49.887
2019-11-14 | 5:19 | 49.886
2019-11-14 | 5:19 | 49.883
2019-11-14 | 5:19 | 49.88
2019-11-14 | 5:19 | 49.877
2019-11-14 | 5:19 | 49.875
2019-11-14 | 5:19 | 49.876
2019-11-14 | 5:19 | 49.876
2019-11-14 | 5:19 | 49.878
2019-11-14 | 5:19 | 49.881
2019-11-14 | 5:19 | 49.88
2019-11-14 | 5:19 | 49.88
2019-11-14 | 5:19 | 49.878
2019-11-14 | 5:19 | 49.876
2019-11-14 | 5:19 | 49.874
2019-11-14 | 5:19 | 49.87
2019-11-14 | 5:19 | 49.867
2019-11-14 | 5:19 | 49.861
2019-11-14 | 5:19 | 49.859
2019-11-14 | 5:19 | 49.857
2019-11-14 | 5:19 | 49.853
2019-11-14 | 5:19 | 49.85
2019-11-14 | 5:19 | 49.849
2019-11-14 | 5:19 | 49.85
2019-11-14 | 5:19 | 49.851
2019-11-14 | 5:19 | 49.851
2019-11-14 | 5:19 | 49.85
2019-11-14 | 5:19 | 49.852
2019-11-14 | 5:19 | 49.853
2019-11-14 | 5:19 | 49.855
2019-11-14 | 5:19 | 49.852
2019-11-14 | 5:19 | 49.851
2019-11-14 | 5:19 | 49.848
2019-11-14 | 5:19 | 49.846
2019-11-14 | 5:19 | 49.842
2019-11-14 | 5:19 | 49.84
2019-11-14 | 5:19 | 49.838
2019-11-14 | 5:19 | 49.838
2019-11-14 | 5:19 | 49.841
2019-11-14 | 5:19 | 49.844
2019-11-14 | 5:19 | 49.847
2019-11-14 | 5:19 | 49.852
2019-11-14 | 5:19 | 49.859
2019-11-14 | 5:20 | 49.868
2019-11-14 | 5:20 | 49.875
2019-11-14 | 5:20 | 49.884
2019-11-14 | 5:20 | 49.898
2019-11-14 | 5:20 | 49.907
2019-11-14 | 5:20 | 49.914
2019-11-14 | 5:20 | 49.919
2019-11-14 | 5:20 | 49.924
2019-11-14 | 5:20 | 49.927
2019-11-14 | 5:20 | 49.93
2019-11-14 | 5:20 | 49.93
2019-11-14 | 5:20 | 49.929
2019-11-14 | 5:20 | 49.927
2019-11-14 | 5:20 | 49.924
2019-11-14 | 5:20 | 49.922
2019-11-14 | 5:20 | 49.919
2019-11-14 | 5:20 | 49.918
2019-11-14 | 5:20 | 49.918
2019-11-14 | 5:20 | 49.92
2019-11-14 | 5:20 | 49.921
2019-11-14 | 5:20 | 49.922
2019-11-14 | 5:20 | 49.923
2019-11-14 | 5:20 | 49.923
2019-11-14 | 5:20 | 49.922
2019-11-14 | 5:20 | 49.922
2019-11-14 | 5:20 | 49.923
2019-11-14 | 5:20 | 49.924
2019-11-14 | 5:20 | 49.924
2019-11-14 | 5:20 | 49.926
2019-11-14 | 5:20 | 49.929
2019-11-14 | 5:20 | 49.93
2019-11-14 | 5:20 | 49.932
2019-11-14 | 5:20 | 49.934
2019-11-14 | 5:20 | 49.935
2019-11-14 | 5:20 | 49.937
2019-11-14 | 5:20 | 49.936
2019-11-14 | 5:20 | 49.937
2019-11-14 | 5:20 | 49.938
2019-11-14 | 5:20 | 49.938
2019-11-14 | 5:20 | 49.94
2019-11-14 | 5:20 | 49.941
2019-11-14 | 5:20 | 49.941
2019-11-14 | 5:20 | 49.941
2019-11-14 | 5:20 | 49.941
2019-11-14 | 5:20 | 49.941
2019-11-14 | 5:20 | 49.941
2019-11-14 | 5:20 | 49.94
2019-11-14 | 5:20 | 49.94
2019-11-14 | 5:20 | 49.941
2019-11-14 | 5:20 | 49.941
2019-11-14 | 5:20 | 49.941
2019-11-14 | 5:20 | 49.942
2019-11-14 | 5:20 | 49.943
2019-11-14 | 5:20 | 49.944
2019-11-14 | 5:20 | 49.944
2019-11-14 | 5:20 | 49.943
2019-11-14 | 5:20 | 49.943
2019-11-14 | 5:20 | 49.943
2019-11-14 | 5:20 | 49.942
2019-11-14 | 5:20 | 49.938
2019-11-14 | 5:20 | 49.938
2019-11-14 | 5:21 | 49.938
2019-11-14 | 5:21 | 49.938
2019-11-14 | 5:21 | 49.938
2019-11-14 | 5:21 | 49.937
2019-11-14 | 5:21 | 49.938
2019-11-14 | 5:21 | 49.938
2019-11-14 | 5:21 | 49.939
2019-11-14 | 5:21 | 49.941
2019-11-14 | 5:21 | 49.943
2019-11-14 | 5:21 | 49.945
2019-11-14 | 5:21 | 49.946
2019-11-14 | 5:21 | 49.948
2019-11-14 | 5:21 | 49.949
2019-11-14 | 5:21 | 49.949
2019-11-14 | 5:21 | 49.947
2019-11-14 | 5:21 | 49.948
2019-11-14 | 5:21 | 49.949
2019-11-14 | 5:21 | 49.951
2019-11-14 | 5:21 | 49.952
2019-11-14 | 5:21 | 49.953
2019-11-14 | 5:21 | 49.954
2019-11-14 | 5:21 | 49.954
2019-11-14 | 5:21 | 49.955
2019-11-14 | 5:21 | 49.956
2019-11-14 | 5:21 | 49.955
2019-11-14 | 5:21 | 49.954
2019-11-14 | 5:21 | 49.952
2019-11-14 | 5:21 | 49.952
2019-11-14 | 5:21 | 49.95
2019-11-14 | 5:21 | 49.95
2019-11-14 | 5:21 | 49.952
2019-11-14 | 5:21 | 49.952
2019-11-14 | 5:21 | 49.952
2019-11-14 | 5:21 | 49.95
2019-11-14 | 5:21 | 49.948
2019-11-14 | 5:21 | 49.946
2019-11-14 | 5:21 | 49.947
2019-11-14 | 5:21 | 49.947
2019-11-14 | 5:21 | 49.947
2019-11-14 | 5:21 | 49.945
2019-11-14 | 5:21 | 49.942
2019-11-14 | 5:21 | 49.939
2019-11-14 | 5:21 | 49.936
2019-11-14 | 5:21 | 49.935
2019-11-14 | 5:21 | 49.935
2019-11-14 | 5:21 | 49.938
2019-11-14 | 5:21 | 49.939
2019-11-14 | 5:21 | 49.943
2019-11-14 | 5:21 | 49.945
2019-11-14 | 5:21 | 49.947
2019-11-14 | 5:21 | 49.95
2019-11-14 | 5:21 | 49.955
2019-11-14 | 5:21 | 49.956
2019-11-14 | 5:21 | 49.955
2019-11-14 | 5:21 | 49.955
2019-11-14 | 5:21 | 49.954
2019-11-14 | 5:21 | 49.954
2019-11-14 | 5:21 | 49.954
2019-11-14 | 5:21 | 49.956
2019-11-14 | 5:22 | 49.958
2019-11-14 | 5:22 | 49.959
2019-11-14 | 5:22 | 49.959
2019-11-14 | 5:22 | 49.959
2019-11-14 | 5:22 | 49.96
2019-11-14 | 5:22 | 49.958
2019-11-14 | 5:22 | 49.956
2019-11-14 | 5:22 | 49.952
2019-11-14 | 5:22 | 49.951
2019-11-14 | 5:22 | 49.949
2019-11-14 | 5:22 | 49.947
2019-11-14 | 5:22 | 49.946
2019-11-14 | 5:22 | 49.946
2019-11-14 | 5:22 | 49.948
2019-11-14 | 5:22 | 49.949
2019-11-14 | 5:22 | 49.949
2019-11-14 | 5:22 | 49.948
2019-11-14 | 5:22 | 49.948
2019-11-14 | 5:22 | 49.95
2019-11-14 | 5:22 | 49.95
2019-11-14 | 5:22 | 49.949
2019-11-14 | 5:22 | 49.948
2019-11-14 | 5:22 | 49.945
2019-11-14 | 5:22 | 49.943
2019-11-14 | 5:22 | 49.941
2019-11-14 | 5:22 | 49.938
2019-11-14 | 5:22 | 49.937
2019-11-14 | 5:22 | 49.934
2019-11-14 | 5:22 | 49.935
2019-11-14 | 5:22 | 49.939
2019-11-14 | 5:22 | 49.942
2019-11-14 | 5:22 | 49.944
2019-11-14 | 5:22 | 49.947
2019-11-14 | 5:22 | 49.948
2019-11-14 | 5:22 | 49.949
2019-11-14 | 5:22 | 49.951
2019-11-14 | 5:22 | 49.95
2019-11-14 | 5:22 | 49.95
2019-11-14 | 5:22 | 49.951
2019-11-14 | 5:22 | 49.951
2019-11-14 | 5:22 | 49.95
2019-11-14 | 5:22 | 49.948
2019-11-14 | 5:22 | 49.947
2019-11-14 | 5:22 | 49.947
2019-11-14 | 5:22 | 49.947
2019-11-14 | 5:22 | 49.947
2019-11-14 | 5:22 | 49.948
2019-11-14 | 5:22 | 49.948
2019-11-14 | 5:22 | 49.95
2019-11-14 | 5:22 | 49.951
2019-11-14 | 5:22 | 49.952
2019-11-14 | 5:22 | 49.953
2019-11-14 | 5:22 | 49.955
2019-11-14 | 5:22 | 49.958
2019-11-14 | 5:22 | 49.961
2019-11-14 | 5:22 | 49.963
2019-11-14 | 5:22 | 49.964
2019-11-14 | 5:22 | 49.964
2019-11-14 | 5:22 | 49.964
2019-11-14 | 5:22 | 49.963
2019-11-14 | 5:22 | 49.962
2019-11-14 | 5:23 | 49.96
2019-11-14 | 5:23 | 49.957
2019-11-14 | 5:23 | 49.956
2019-11-14 | 5:23 | 49.955
2019-11-14 | 5:23 | 49.954
2019-11-14 | 5:23 | 49.951
2019-11-14 | 5:23 | 49.948
2019-11-14 | 5:23 | 49.948
2019-11-14 | 5:23 | 49.946
2019-11-14 | 5:23 | 49.945
2019-11-14 | 5:23 | 49.945
2019-11-14 | 5:23 | 49.946
2019-11-14 | 5:23 | 49.946
2019-11-14 | 5:23 | 49.948
2019-11-14 | 5:23 | 49.951
2019-11-14 | 5:23 | 49.952
2019-11-14 | 5:23 | 49.954
2019-11-14 | 5:23 | 49.956
2019-11-14 | 5:23 | 49.956
2019-11-14 | 5:23 | 49.956
2019-11-14 | 5:23 | 49.956
2019-11-14 | 5:23 | 49.954
2019-11-14 | 5:23 | 49.954
2019-11-14 | 5:23 | 49.953
2019-11-14 | 5:23 | 49.952
2019-11-14 | 5:23 | 49.952
2019-11-14 | 5:23 | 49.953
2019-11-14 | 5:23 | 49.954
2019-11-14 | 5:23 | 49.953
2019-11-14 | 5:23 | 49.952
2019-11-14 | 5:23 | 49.952
2019-11-14 | 5:23 | 49.95
2019-11-14 | 5:23 | 49.947
2019-11-14 | 5:23 | 49.946
2019-11-14 | 5:23 | 49.946
2019-11-14 | 5:23 | 49.944
2019-11-14 | 5:23 | 49.944
2019-11-14 | 5:23 | 49.942
2019-11-14 | 5:23 | 49.94
2019-11-14 | 5:23 | 49.94
2019-11-14 | 5:23 | 49.939
2019-11-14 | 5:23 | 49.939
2019-11-14 | 5:23 | 49.937
2019-11-14 | 5:23 | 49.936
2019-11-14 | 5:23 | 49.934
2019-11-14 | 5:23 | 49.935
2019-11-14 | 5:23 | 49.936
2019-11-14 | 5:23 | 49.937
2019-11-14 | 5:23 | 49.938
2019-11-14 | 5:23 | 49.936
2019-11-14 | 5:23 | 49.934
2019-11-14 | 5:23 | 49.933
2019-11-14 | 5:23 | 49.933
2019-11-14 | 5:23 | 49.932
2019-11-14 | 5:23 | 49.932
2019-11-14 | 5:23 | 49.931
2019-11-14 | 5:23 | 49.931
2019-11-14 | 5:23 | 49.931
2019-11-14 | 5:23 | 49.933
2019-11-14 | 5:24 | 49.934
2019-11-14 | 5:24 | 49.934
2019-11-14 | 5:24 | 49.936
2019-11-14 | 5:24 | 49.937
2019-11-14 | 5:24 | 49.938
2019-11-14 | 5:24 | 49.938
2019-11-14 | 5:24 | 49.939
2019-11-14 | 5:24 | 49.938
2019-11-14 | 5:24 | 49.94
2019-11-14 | 5:24 | 49.94
2019-11-14 | 5:24 | 49.938
2019-11-14 | 5:24 | 49.934
2019-11-14 | 5:24 | 49.93
2019-11-14 | 5:24 | 49.929
2019-11-14 | 5:24 | 49.928
2019-11-14 | 5:24 | 49.928
2019-11-14 | 5:24 | 49.929
2019-11-14 | 5:24 | 49.93
2019-11-14 | 5:24 | 49.93
2019-11-14 | 5:24 | 49.93
2019-11-14 | 5:24 | 49.932
2019-11-14 | 5:24 | 49.932
2019-11-14 | 5:24 | 49.932
2019-11-14 | 5:24 | 49.93
2019-11-14 | 5:24 | 49.926
2019-11-14 | 5:24 | 49.924
2019-11-14 | 5:24 | 49.924
2019-11-14 | 5:24 | 49.926
2019-11-14 | 5:24 | 49.929
2019-11-14 | 5:24 | 49.931
2019-11-14 | 5:24 | 49.932
2019-11-14 | 5:24 | 49.935
2019-11-14 | 5:24 | 49.935
2019-11-14 | 5:24 | 49.939
2019-11-14 | 5:24 | 49.94
2019-11-14 | 5:24 | 49.942
2019-11-14 | 5:24 | 49.941
2019-11-14 | 5:24 | 49.94
2019-11-14 | 5:24 | 49.94
2019-11-14 | 5:24 | 49.94
2019-11-14 | 5:24 | 49.942
2019-11-14 | 5:24 | 49.944
2019-11-14 | 5:24 | 49.945
2019-11-14 | 5:24 | 49.948
2019-11-14 | 5:24 | 49.95
2019-11-14 | 5:24 | 49.951
2019-11-14 | 5:24 | 49.951
2019-11-14 | 5:24 | 49.952
2019-11-14 | 5:24 | 49.951
2019-11-14 | 5:24 | 49.949
2019-11-14 | 5:24 | 49.945
2019-11-14 | 5:24 | 49.942
2019-11-14 | 5:24 | 49.94
2019-11-14 | 5:24 | 49.937
2019-11-14 | 5:24 | 49.935
2019-11-14 | 5:24 | 49.933
2019-11-14 | 5:24 | 49.932
2019-11-14 | 5:24 | 49.936
2019-11-14 | 5:24 | 49.94
2019-11-14 | 5:24 | 49.944
2019-11-14 | 5:24 | 49.947
2019-11-14 | 5:25 | 49.951
2019-11-14 | 5:25 | 49.953
2019-11-14 | 5:25 | 49.952
2019-11-14 | 5:25 | 49.952
2019-11-14 | 5:25 | 49.951
2019-11-14 | 5:25 | 49.949
2019-11-14 | 5:25 | 49.946
2019-11-14 | 5:25 | 49.942
2019-11-14 | 5:25 | 49.941
2019-11-14 | 5:25 | 49.939
2019-11-14 | 5:25 | 49.939
2019-11-14 | 5:25 | 49.941
2019-11-14 | 5:25 | 49.941
2019-11-14 | 5:25 | 49.944
2019-11-14 | 5:25 | 49.947
2019-11-14 | 5:25 | 49.95
2019-11-14 | 5:25 | 49.952
2019-11-14 | 5:25 | 49.955
2019-11-14 | 5:25 | 49.956
2019-11-14 | 5:25 | 49.958
2019-11-14 | 5:25 | 49.96
2019-11-14 | 5:25 | 49.961
2019-11-14 | 5:25 | 49.962
2019-11-14 | 5:25 | 49.965
2019-11-14 | 5:25 | 49.967
2019-11-14 | 5:25 | 49.968
2019-11-14 | 5:25 | 49.967
2019-11-14 | 5:25 | 49.966
2019-11-14 | 5:25 | 49.967
2019-11-14 | 5:25 | 49.966
2019-11-14 | 5:25 | 49.966
2019-11-14 | 5:25 | 49.962
2019-11-14 | 5:25 | 49.962
2019-11-14 | 5:25 | 49.961
2019-11-14 | 5:25 | 49.962
2019-11-14 | 5:25 | 49.964
2019-11-14 | 5:25 | 49.964
2019-11-14 | 5:25 | 49.966
2019-11-14 | 5:25 | 49.967
2019-11-14 | 5:25 | 49.97
2019-11-14 | 5:25 | 49.969
2019-11-14 | 5:25 | 49.968
2019-11-14 | 5:25 | 49.968
2019-11-14 | 5:25 | 49.966
2019-11-14 | 5:25 | 49.967
2019-11-14 | 5:25 | 49.969
2019-11-14 | 5:25 | 49.97
2019-11-14 | 5:25 | 49.971
2019-11-14 | 5:25 | 49.972
2019-11-14 | 5:25 | 49.972
2019-11-14 | 5:25 | 49.97
2019-11-14 | 5:25 | 49.97
2019-11-14 | 5:25 | 49.968
2019-11-14 | 5:25 | 49.967
2019-11-14 | 5:25 | 49.966
2019-11-14 | 5:25 | 49.965
2019-11-14 | 5:25 | 49.965
2019-11-14 | 5:25 | 49.965
2019-11-14 | 5:25 | 49.965
2019-11-14 | 5:26 | 49.964
2019-11-14 | 5:26 | 49.964
2019-11-14 | 5:26 | 49.962
2019-11-14 | 5:26 | 49.963
2019-11-14 | 5:26 | 49.963
2019-11-14 | 5:26 | 49.962
2019-11-14 | 5:26 | 49.962
2019-11-14 | 5:26 | 49.962
2019-11-14 | 5:26 | 49.961
2019-11-14 | 5:26 | 49.963
2019-11-14 | 5:26 | 49.963
2019-11-14 | 5:26 | 49.962
2019-11-14 | 5:26 | 49.961
2019-11-14 | 5:26 | 49.959
2019-11-14 | 5:26 | 49.957
2019-11-14 | 5:26 | 49.955
2019-11-14 | 5:26 | 49.954
2019-11-14 | 5:26 | 49.951
2019-11-14 | 5:26 | 49.948
2019-11-14 | 5:26 | 49.944
2019-11-14 | 5:26 | 49.942
2019-11-14 | 5:26 | 49.942
2019-11-14 | 5:26 | 49.943
2019-11-14 | 5:26 | 49.946
2019-11-14 | 5:26 | 49.948
2019-11-14 | 5:26 | 49.95
2019-11-14 | 5:26 | 49.949
2019-11-14 | 5:26 | 49.95
2019-11-14 | 5:26 | 49.95
2019-11-14 | 5:26 | 49.952
2019-11-14 | 5:26 | 49.952
2019-11-14 | 5:26 | 49.951
2019-11-14 | 5:26 | 49.951
2019-11-14 | 5:26 | 49.953
2019-11-14 | 5:26 | 49.953
2019-11-14 | 5:26 | 49.952
2019-11-14 | 5:26 | 49.953
2019-11-14 | 5:26 | 49.953
2019-11-14 | 5:26 | 49.954
2019-11-14 | 5:26 | 49.953
2019-11-14 | 5:26 | 49.955
2019-11-14 | 5:26 | 49.957
2019-11-14 | 5:26 | 49.958
2019-11-14 | 5:26 | 49.962
2019-11-14 | 5:26 | 49.966
2019-11-14 | 5:26 | 49.969
2019-11-14 | 5:26 | 49.971
2019-11-14 | 5:26 | 49.971
2019-11-14 | 5:26 | 49.972
2019-11-14 | 5:26 | 49.972
2019-11-14 | 5:26 | 49.973
2019-11-14 | 5:26 | 49.974
2019-11-14 | 5:26 | 49.974
2019-11-14 | 5:26 | 49.976
2019-11-14 | 5:26 | 49.979
2019-11-14 | 5:26 | 49.982
2019-11-14 | 5:26 | 49.982
2019-11-14 | 5:26 | 49.984
2019-11-14 | 5:26 | 49.985
2019-11-14 | 5:26 | 49.984
2019-11-14 | 5:26 | 49.986
2019-11-14 | 5:27 | 49.986
2019-11-14 | 5:27 | 49.987
2019-11-14 | 5:27 | 49.988
2019-11-14 | 5:27 | 49.986
2019-11-14 | 5:27 | 49.987
2019-11-14 | 5:27 | 49.987
2019-11-14 | 5:27 | 49.988
2019-11-14 | 5:27 | 49.988
2019-11-14 | 5:27 | 49.988
2019-11-14 | 5:27 | 49.987
2019-11-14 | 5:27 | 49.988
2019-11-14 | 5:27 | 49.988
2019-11-14 | 5:27 | 49.988
2019-11-14 | 5:27 | 49.989
2019-11-14 | 5:27 | 49.988
2019-11-14 | 5:27 | 49.987
2019-11-14 | 5:27 | 49.986
2019-11-14 | 5:27 | 49.986
2019-11-14 | 5:27 | 49.988
2019-11-14 | 5:27 | 49.991
2019-11-14 | 5:27 | 49.993
2019-11-14 | 5:27 | 49.996
2019-11-14 | 5:27 | 49.997
2019-11-14 | 5:27 | 49.996
2019-11-14 | 5:27 | 49.995
2019-11-14 | 5:27 | 49.995
2019-11-14 | 5:27 | 49.994
2019-11-14 | 5:27 | 49.991
2019-11-14 | 5:27 | 49.987
2019-11-14 | 5:27 | 49.983
2019-11-14 | 5:27 | 49.981
2019-11-14 | 5:27 | 49.967
2019-11-14 | 5:27 | 49.952
2019-11-14 | 5:27 | 49.943
2019-11-14 | 5:27 | 49.938
2019-11-14 | 5:27 | 49.934
2019-11-14 | 5:27 | 49.931
2019-11-14 | 5:27 | 49.929
2019-11-14 | 5:27 | 49.927
2019-11-14 | 5:27 | 49.925
2019-11-14 | 5:27 | 49.922
2019-11-14 | 5:27 | 49.922
2019-11-14 | 5:27 | 49.919
2019-11-14 | 5:27 | 49.923
2019-11-14 | 5:27 | 49.923
2019-11-14 | 5:27 | 49.927
2019-11-14 | 5:27 | 49.929
2019-11-14 | 5:27 | 49.933
2019-11-14 | 5:27 | 49.938
2019-11-14 | 5:27 | 49.944
2019-11-14 | 5:27 | 49.947
2019-11-14 | 5:27 | 49.948
2019-11-14 | 5:27 | 49.947
2019-11-14 | 5:27 | 49.946
2019-11-14 | 5:27 | 49.945
2019-11-14 | 5:27 | 49.943
2019-11-14 | 5:27 | 49.941
2019-11-14 | 5:27 | 49.937
2019-11-14 | 5:27 | 49.934
2019-11-14 | 5:28 | 49.931
2019-11-14 | 5:28 | 49.927
2019-11-14 | 5:28 | 49.924
2019-11-14 | 5:28 | 49.92
2019-11-14 | 5:28 | 49.919
2019-11-14 | 5:28 | 49.918
2019-11-14 | 5:28 | 49.92
2019-11-14 | 5:28 | 49.919
2019-11-14 | 5:28 | 49.919
2019-11-14 | 5:28 | 49.92
2019-11-14 | 5:28 | 49.919
2019-11-14 | 5:28 | 49.921
2019-11-14 | 5:28 | 49.924
2019-11-14 | 5:28 | 49.927
2019-11-14 | 5:28 | 49.929
2019-11-14 | 5:28 | 49.931
2019-11-14 | 5:28 | 49.933
2019-11-14 | 5:28 | 49.936
2019-11-14 | 5:28 | 49.937
2019-11-14 | 5:28 | 49.939
2019-11-14 | 5:28 | 49.938
2019-11-14 | 5:28 | 49.939
2019-11-14 | 5:28 | 49.939
2019-11-14 | 5:28 | 49.94
2019-11-14 | 5:28 | 49.941
2019-11-14 | 5:28 | 49.94
2019-11-14 | 5:28 | 49.94
2019-11-14 | 5:28 | 49.938
2019-11-14 | 5:28 | 49.937
2019-11-14 | 5:28 | 49.937
2019-11-14 | 5:28 | 49.935
2019-11-14 | 5:28 | 49.935
2019-11-14 | 5:28 | 49.936
2019-11-14 | 5:28 | 49.938
2019-11-14 | 5:28 | 49.939
2019-11-14 | 5:28 | 49.938
2019-11-14 | 5:28 | 49.94
2019-11-14 | 5:28 | 49.941
2019-11-14 | 5:28 | 49.942
2019-11-14 | 5:28 | 49.943
2019-11-14 | 5:28 | 49.943
2019-11-14 | 5:28 | 49.944
2019-11-14 | 5:28 | 49.943
2019-11-14 | 5:28 | 49.942
2019-11-14 | 5:28 | 49.94
2019-11-14 | 5:28 | 49.939
2019-11-14 | 5:28 | 49.939
2019-11-14 | 5:28 | 49.94
2019-11-14 | 5:28 | 49.941
2019-11-14 | 5:28 | 49.943
2019-11-14 | 5:28 | 49.946
2019-11-14 | 5:28 | 49.949
2019-11-14 | 5:28 | 49.951
2019-11-14 | 5:28 | 49.952
2019-11-14 | 5:28 | 49.951
2019-11-14 | 5:28 | 49.952
2019-11-14 | 5:28 | 49.951
2019-11-14 | 5:28 | 49.952
2019-11-14 | 5:28 | 49.952
2019-11-14 | 5:28 | 49.953
2019-11-14 | 5:28 | 49.953
2019-11-14 | 5:29 | 49.954
2019-11-14 | 5:29 | 49.952
2019-11-14 | 5:29 | 49.952
2019-11-14 | 5:29 | 49.952
2019-11-14 | 5:29 | 49.951
2019-11-14 | 5:29 | 49.946
2019-11-14 | 5:29 | 49.95
2019-11-14 | 5:29 | 49.951
2019-11-14 | 5:29 | 49.95
2019-11-14 | 5:29 | 49.951
2019-11-14 | 5:29 | 49.95
2019-11-14 | 5:29 | 49.948
2019-11-14 | 5:29 | 49.947
2019-11-14 | 5:29 | 49.944
2019-11-14 | 5:29 | 49.94
2019-11-14 | 5:29 | 49.938
2019-11-14 | 5:29 | 49.936
2019-11-14 | 5:29 | 49.936
2019-11-14 | 5:29 | 49.935
2019-11-14 | 5:29 | 49.934
2019-11-14 | 5:29 | 49.935
2019-11-14 | 5:29 | 49.934
2019-11-14 | 5:29 | 49.934
2019-11-14 | 5:29 | 49.933
2019-11-14 | 5:29 | 49.932
2019-11-14 | 5:29 | 49.932
2019-11-14 | 5:29 | 49.931
2019-11-14 | 5:29 | 49.931
2019-11-14 | 5:29 | 49.932
2019-11-14 | 5:29 | 49.931
2019-11-14 | 5:29 | 49.931
2019-11-14 | 5:29 | 49.932
2019-11-14 | 5:29 | 49.934
2019-11-14 | 5:29 | 49.934
2019-11-14 | 5:29 | 49.935
2019-11-14 | 5:29 | 49.934
2019-11-14 | 5:29 | 49.934
2019-11-14 | 5:29 | 49.933
2019-11-14 | 5:29 | 49.933
2019-11-14 | 5:29 | 49.931
2019-11-14 | 5:29 | 49.93
2019-11-14 | 5:29 | 49.93
2019-11-14 | 5:29 | 49.93
2019-11-14 | 5:29 | 49.93
2019-11-14 | 5:29 | 49.929
2019-11-14 | 5:29 | 49.928
2019-11-14 | 5:29 | 49.927
2019-11-14 | 5:29 | 49.928
2019-11-14 | 5:29 | 49.929
2019-11-14 | 5:29 | 49.927
2019-11-14 | 5:29 | 49.926
2019-11-14 | 5:29 | 49.926
2019-11-14 | 5:29 | 49.926
2019-11-14 | 5:29 | 49.927
2019-11-14 | 5:29 | 49.927
2019-11-14 | 5:29 | 49.928
2019-11-14 | 5:29 | 49.928
2019-11-14 | 5:29 | 49.93
2019-11-14 | 5:29 | 49.931
2019-11-14 | 5:30 | 49.929
2019-11-14 | 5:30 | 49.929
2019-11-14 | 5:30 | 49.929
2019-11-14 | 5:30 | 49.928
2019-11-14 | 5:30 | 49.929
2019-11-14 | 5:30 | 49.928
2019-11-14 | 5:30 | 49.928
2019-11-14 | 5:30 | 49.927
2019-11-14 | 5:30 | 49.926
2019-11-14 | 5:30 | 49.925
2019-11-14 | 5:30 | 49.925
2019-11-14 | 5:30 | 49.927
2019-11-14 | 5:30 | 49.93
2019-11-14 | 5:30 | 49.933
2019-11-14 | 5:30 | 49.936
2019-11-14 | 5:30 | 49.936
2019-11-14 | 5:30 | 49.936
2019-11-14 | 5:30 | 49.936
2019-11-14 | 5:30 | 49.937
2019-11-14 | 5:30 | 49.939
2019-11-14 | 5:30 | 49.939
2019-11-14 | 5:30 | 49.94
2019-11-14 | 5:30 | 49.94
2019-11-14 | 5:30 | 49.943
2019-11-14 | 5:30 | 49.945
2019-11-14 | 5:30 | 49.945
2019-11-14 | 5:30 | 49.944
2019-11-14 | 5:30 | 49.944
2019-11-14 | 5:30 | 49.945
2019-11-14 | 5:30 | 49.946
2019-11-14 | 5:30 | 49.945
2019-11-14 | 5:30 | 49.945
2019-11-14 | 5:30 | 49.944
2019-11-14 | 5:30 | 49.943
2019-11-14 | 5:30 | 49.942
2019-11-14 | 5:30 | 49.941
2019-11-14 | 5:30 | 49.94
2019-11-14 | 5:30 | 49.939
2019-11-14 | 5:30 | 49.939
2019-11-14 | 5:30 | 49.938
2019-11-14 | 5:30 | 49.937
2019-11-14 | 5:30 | 49.937
2019-11-14 | 5:30 | 49.935
2019-11-14 | 5:30 | 49.936
2019-11-14 | 5:30 | 49.935
2019-11-14 | 5:30 | 49.936
2019-11-14 | 5:30 | 49.937
2019-11-14 | 5:30 | 49.937
2019-11-14 | 5:30 | 49.937
2019-11-14 | 5:30 | 49.935
2019-11-14 | 5:30 | 49.934
2019-11-14 | 5:30 | 49.934
2019-11-14 | 5:30 | 49.935
2019-11-14 | 5:30 | 49.937
2019-11-14 | 5:30 | 49.94
2019-11-14 | 5:30 | 49.942
2019-11-14 | 5:30 | 49.945
2019-11-14 | 5:30 | 49.949
2019-11-14 | 5:30 | 49.952
2019-11-14 | 5:30 | 49.955
2019-11-14 | 5:30 | 49.958
2019-11-14 | 5:31 | 49.96
2019-11-14 | 5:31 | 49.961
2019-11-14 | 5:31 | 49.961
2019-11-14 | 5:31 | 49.96
2019-11-14 | 5:31 | 49.96
2019-11-14 | 5:31 | 49.96
2019-11-14 | 5:31 | 49.96
2019-11-14 | 5:31 | 49.959
2019-11-14 | 5:31 | 49.957
2019-11-14 | 5:31 | 49.954
2019-11-14 | 5:31 | 49.952
2019-11-14 | 5:31 | 49.95
2019-11-14 | 5:31 | 49.949
2019-11-14 | 5:31 | 49.949
2019-11-14 | 5:31 | 49.948
2019-11-14 | 5:31 | 49.949
2019-11-14 | 5:31 | 49.951
2019-11-14 | 5:31 | 49.953
2019-11-14 | 5:31 | 49.955
2019-11-14 | 5:31 | 49.956
2019-11-14 | 5:31 | 49.956
2019-11-14 | 5:31 | 49.954
2019-11-14 | 5:31 | 49.954
2019-11-14 | 5:31 | 49.954
2019-11-14 | 5:31 | 49.951
2019-11-14 | 5:31 | 49.949
2019-11-14 | 5:31 | 49.95
2019-11-14 | 5:31 | 49.948
2019-11-14 | 5:31 | 49.95
2019-11-14 | 5:31 | 49.951
2019-11-14 | 5:31 | 49.953
2019-11-14 | 5:31 | 49.956
2019-11-14 | 5:31 | 49.958
2019-11-14 | 5:31 | 49.96
2019-11-14 | 5:31 | 49.964
2019-11-14 | 5:31 | 49.967
2019-11-14 | 5:31 | 49.967
2019-11-14 | 5:31 | 49.966
2019-11-14 | 5:31 | 49.967
2019-11-14 | 5:31 | 49.966
2019-11-14 | 5:31 | 49.964
2019-11-14 | 5:31 | 49.96
2019-11-14 | 5:31 | 49.958
2019-11-14 | 5:31 | 49.955
2019-11-14 | 5:31 | 49.955
2019-11-14 | 5:31 | 49.952
2019-11-14 | 5:31 | 49.953
2019-11-14 | 5:31 | 49.952
2019-11-14 | 5:31 | 49.953
2019-11-14 | 5:31 | 49.953
2019-11-14 | 5:31 | 49.956
2019-11-14 | 5:31 | 49.959
2019-11-14 | 5:31 | 49.96
2019-11-14 | 5:31 | 49.962
2019-11-14 | 5:31 | 49.965
2019-11-14 | 5:31 | 49.965
2019-11-14 | 5:31 | 49.967
2019-11-14 | 5:31 | 49.969
2019-11-14 | 5:31 | 49.97
2019-11-14 | 5:32 | 49.972
2019-11-14 | 5:32 | 49.972
2019-11-14 | 5:32 | 49.971
2019-11-14 | 5:32 | 49.974
2019-11-14 | 5:32 | 49.972
2019-11-14 | 5:32 | 49.971
2019-11-14 | 5:32 | 49.97
2019-11-14 | 5:32 | 49.969
2019-11-14 | 5:32 | 49.968
2019-11-14 | 5:32 | 49.966
2019-11-14 | 5:32 | 49.966
2019-11-14 | 5:32 | 49.966
2019-11-14 | 5:32 | 49.966
2019-11-14 | 5:32 | 49.964
2019-11-14 | 5:32 | 49.964
2019-11-14 | 5:32 | 49.963
2019-11-14 | 5:32 | 49.962
2019-11-14 | 5:32 | 49.961
2019-11-14 | 5:32 | 49.96
2019-11-14 | 5:32 | 49.959
2019-11-14 | 5:32 | 49.957
2019-11-14 | 5:32 | 49.957
2019-11-14 | 5:32 | 49.955
2019-11-14 | 5:32 | 49.956
2019-11-14 | 5:32 | 49.955
2019-11-14 | 5:32 | 49.954
2019-11-14 | 5:32 | 49.953
2019-11-14 | 5:32 | 49.952
2019-11-14 | 5:32 | 49.952
2019-11-14 | 5:32 | 49.953
2019-11-14 | 5:32 | 49.953
2019-11-14 | 5:32 | 49.953
2019-11-14 | 5:32 | 49.953
2019-11-14 | 5:32 | 49.956
2019-11-14 | 5:32 | 49.957
2019-11-14 | 5:32 | 49.957
2019-11-14 | 5:32 | 49.957
2019-11-14 | 5:32 | 49.956
2019-11-14 | 5:32 | 49.956
2019-11-14 | 5:32 | 49.955
2019-11-14 | 5:32 | 49.955
2019-11-14 | 5:32 | 49.954
2019-11-14 | 5:32 | 49.954
2019-11-14 | 5:32 | 49.952
2019-11-14 | 5:32 | 49.951
2019-11-14 | 5:32 | 49.951
2019-11-14 | 5:32 | 49.95
2019-11-14 | 5:32 | 49.952
2019-11-14 | 5:32 | 49.952
2019-11-14 | 5:32 | 49.952
2019-11-14 | 5:32 | 49.954
2019-11-14 | 5:32 | 49.955
2019-11-14 | 5:32 | 49.957
2019-11-14 | 5:32 | 49.959
2019-11-14 | 5:32 | 49.958
2019-11-14 | 5:32 | 49.959
2019-11-14 | 5:32 | 49.957
2019-11-14 | 5:32 | 49.956
2019-11-14 | 5:32 | 49.955
2019-11-14 | 5:32 | 49.955
2019-11-14 | 5:32 | 49.958
2019-11-14 | 5:33 | 49.958
2019-11-14 | 5:33 | 49.958
2019-11-14 | 5:33 | 49.958
2019-11-14 | 5:33 | 49.958
2019-11-14 | 5:33 | 49.957
2019-11-14 | 5:33 | 49.955
2019-11-14 | 5:33 | 49.954
2019-11-14 | 5:33 | 49.953
2019-11-14 | 5:33 | 49.952
2019-11-14 | 5:33 | 49.949
2019-11-14 | 5:33 | 49.948
2019-11-14 | 5:33 | 49.946
2019-11-14 | 5:33 | 49.946
2019-11-14 | 5:33 | 49.944
2019-11-14 | 5:33 | 49.944
2019-11-14 | 5:33 | 49.945
2019-11-14 | 5:33 | 49.945
2019-11-14 | 5:33 | 49.944
2019-11-14 | 5:33 | 49.944
2019-11-14 | 5:33 | 49.943
2019-11-14 | 5:33 | 49.942
2019-11-14 | 5:33 | 49.943
2019-11-14 | 5:33 | 49.941
2019-11-14 | 5:33 | 49.942
2019-11-14 | 5:33 | 49.944
2019-11-14 | 5:33 | 49.945
2019-11-14 | 5:33 | 49.944
2019-11-14 | 5:33 | 49.945
2019-11-14 | 5:33 | 49.943
2019-11-14 | 5:33 | 49.941
2019-11-14 | 5:33 | 49.938
2019-11-14 | 5:33 | 49.935
2019-11-14 | 5:33 | 49.934
2019-11-14 | 5:33 | 49.932
2019-11-14 | 5:33 | 49.934
2019-11-14 | 5:33 | 49.933
2019-11-14 | 5:33 | 49.935
2019-11-14 | 5:33 | 49.934
2019-11-14 | 5:33 | 49.936
2019-11-14 | 5:33 | 49.936
2019-11-14 | 5:33 | 49.939
2019-11-14 | 5:33 | 49.939
2019-11-14 | 5:33 | 49.94
2019-11-14 | 5:33 | 49.94
2019-11-14 | 5:33 | 49.94
2019-11-14 | 5:33 | 49.94
2019-11-14 | 5:33 | 49.941
2019-11-14 | 5:33 | 49.942
2019-11-14 | 5:33 | 49.944
2019-11-14 | 5:33 | 49.944
2019-11-14 | 5:33 | 49.945
2019-11-14 | 5:33 | 49.946
2019-11-14 | 5:33 | 49.946
2019-11-14 | 5:33 | 49.947
2019-11-14 | 5:33 | 49.946
2019-11-14 | 5:33 | 49.944
2019-11-14 | 5:33 | 49.944
2019-11-14 | 5:33 | 49.944
2019-11-14 | 5:33 | 49.946
2019-11-14 | 5:34 | 49.944
2019-11-14 | 5:34 | 49.944
2019-11-14 | 5:34 | 49.942
2019-11-14 | 5:34 | 49.942
2019-11-14 | 5:34 | 49.942
2019-11-14 | 5:34 | 49.94
2019-11-14 | 5:34 | 49.939
2019-11-14 | 5:34 | 49.938
2019-11-14 | 5:34 | 49.936
2019-11-14 | 5:34 | 49.935
2019-11-14 | 5:34 | 49.937
2019-11-14 | 5:34 | 49.937
2019-11-14 | 5:34 | 49.939
2019-11-14 | 5:34 | 49.94
2019-11-14 | 5:34 | 49.941
2019-11-14 | 5:34 | 49.943
2019-11-14 | 5:34 | 49.944
2019-11-14 | 5:34 | 49.945
2019-11-14 | 5:34 | 49.945
2019-11-14 | 5:34 | 49.945
2019-11-14 | 5:34 | 49.945
2019-11-14 | 5:34 | 49.946
2019-11-14 | 5:34 | 49.947
2019-11-14 | 5:34 | 49.948
2019-11-14 | 5:34 | 49.95
2019-11-14 | 5:34 | 49.951
2019-11-14 | 5:34 | 49.953
2019-11-14 | 5:34 | 49.955
2019-11-14 | 5:34 | 49.956
2019-11-14 | 5:34 | 49.956
2019-11-14 | 5:34 | 49.953
2019-11-14 | 5:34 | 49.954
2019-11-14 | 5:34 | 49.954
2019-11-14 | 5:34 | 49.954
2019-11-14 | 5:34 | 49.953
2019-11-14 | 5:34 | 49.953
2019-11-14 | 5:34 | 49.952
2019-11-14 | 5:34 | 49.952
2019-11-14 | 5:34 | 49.952
2019-11-14 | 5:34 | 49.951
2019-11-14 | 5:34 | 49.95
2019-11-14 | 5:34 | 49.95
2019-11-14 | 5:34 | 49.95
2019-11-14 | 5:34 | 49.95
2019-11-14 | 5:34 | 49.948
2019-11-14 | 5:34 | 49.948
2019-11-14 | 5:34 | 49.949
2019-11-14 | 5:34 | 49.954
2019-11-14 | 5:34 | 49.958
2019-11-14 | 5:34 | 49.963
2019-11-14 | 5:34 | 49.968
2019-11-14 | 5:34 | 49.972
2019-11-14 | 5:34 | 49.976
2019-11-14 | 5:34 | 49.977
2019-11-14 | 5:34 | 49.98
2019-11-14 | 5:34 | 49.978
2019-11-14 | 5:34 | 49.975
2019-11-14 | 5:34 | 49.973
2019-11-14 | 5:34 | 49.969
2019-11-14 | 5:34 | 49.968
2019-11-14 | 5:34 | 49.966
2019-11-14 | 5:35 | 49.965
2019-11-14 | 5:35 | 49.962
2019-11-14 | 5:35 | 49.961
2019-11-14 | 5:35 | 49.962
2019-11-14 | 5:35 | 49.961
2019-11-14 | 5:35 | 49.961
2019-11-14 | 5:35 | 49.96
2019-11-14 | 5:35 | 49.96
2019-11-14 | 5:35 | 49.961
2019-11-14 | 5:35 | 49.962
2019-11-14 | 5:35 | 49.963
2019-11-14 | 5:35 | 49.964
2019-11-14 | 5:35 | 49.963
2019-11-14 | 5:35 | 49.963
2019-11-14 | 5:35 | 49.963
2019-11-14 | 5:35 | 49.962
2019-11-14 | 5:35 | 49.963
2019-11-14 | 5:35 | 49.963
2019-11-14 | 5:35 | 49.965
2019-11-14 | 5:35 | 49.966
2019-11-14 | 5:35 | 49.968
2019-11-14 | 5:35 | 49.969
2019-11-14 | 5:35 | 49.972
2019-11-14 | 5:35 | 49.971
2019-11-14 | 5:35 | 49.971
2019-11-14 | 5:35 | 49.971
2019-11-14 | 5:35 | 49.97
2019-11-14 | 5:35 | 49.969
2019-11-14 | 5:35 | 49.969
2019-11-14 | 5:35 | 49.969
2019-11-14 | 5:35 | 49.971
2019-11-14 | 5:35 | 49.972
2019-11-14 | 5:35 | 49.971
2019-11-14 | 5:35 | 49.971
2019-11-14 | 5:35 | 49.972
2019-11-14 | 5:35 | 49.972
2019-11-14 | 5:35 | 49.972
2019-11-14 | 5:35 | 49.971
2019-11-14 | 5:35 | 49.969
2019-11-14 | 5:35 | 49.966
2019-11-14 | 5:35 | 49.964
2019-11-14 | 5:35 | 49.964
2019-11-14 | 5:35 | 49.964
2019-11-14 | 5:35 | 49.962
2019-11-14 | 5:35 | 49.961
2019-11-14 | 5:35 | 49.959
2019-11-14 | 5:35 | 49.956
2019-11-14 | 5:35 | 49.953
2019-11-14 | 5:35 | 49.952
2019-11-14 | 5:35 | 49.951
2019-11-14 | 5:35 | 49.951
2019-11-14 | 5:35 | 49.952
2019-11-14 | 5:35 | 49.954
2019-11-14 | 5:35 | 49.957
2019-11-14 | 5:35 | 49.958
2019-11-14 | 5:35 | 49.96
2019-11-14 | 5:35 | 49.961
2019-11-14 | 5:35 | 49.962
2019-11-14 | 5:35 | 49.962
2019-11-14 | 5:36 | 49.961
2019-11-14 | 5:36 | 49.962
2019-11-14 | 5:36 | 49.962
2019-11-14 | 5:36 | 49.963
2019-11-14 | 5:36 | 49.962
2019-11-14 | 5:36 | 49.962
2019-11-14 | 5:36 | 49.962
2019-11-14 | 5:36 | 49.961
2019-11-14 | 5:36 | 49.962
2019-11-14 | 5:36 | 49.962
2019-11-14 | 5:36 | 49.963
2019-11-14 | 5:36 | 49.964
2019-11-14 | 5:36 | 49.965
2019-11-14 | 5:36 | 49.967
2019-11-14 | 5:36 | 49.967
2019-11-14 | 5:36 | 49.97
2019-11-14 | 5:36 | 49.971
2019-11-14 | 5:36 | 49.972
2019-11-14 | 5:36 | 49.974
2019-11-14 | 5:36 | 49.973
2019-11-14 | 5:36 | 49.974
2019-11-14 | 5:36 | 49.974
2019-11-14 | 5:36 | 49.975
2019-11-14 | 5:36 | 49.976
2019-11-14 | 5:36 | 49.975
2019-11-14 | 5:36 | 49.976
2019-11-14 | 5:36 | 49.977
2019-11-14 | 5:36 | 49.978
2019-11-14 | 5:36 | 49.981
2019-11-14 | 5:36 | 49.982
2019-11-14 | 5:36 | 49.982
2019-11-14 | 5:36 | 49.982
2019-11-14 | 5:36 | 49.982
2019-11-14 | 5:36 | 49.984
2019-11-14 | 5:36 | 49.984
2019-11-14 | 5:36 | 49.987
2019-11-14 | 5:36 | 49.986
2019-11-14 | 5:36 | 49.988
2019-11-14 | 5:36 | 49.988
2019-11-14 | 5:36 | 49.988
2019-11-14 | 5:36 | 49.988
2019-11-14 | 5:36 | 49.989
2019-11-14 | 5:36 | 49.988
2019-11-14 | 5:36 | 49.987
2019-11-14 | 5:36 | 49.986
2019-11-14 | 5:36 | 49.985
2019-11-14 | 5:36 | 49.984
2019-11-14 | 5:36 | 49.985
2019-11-14 | 5:36 | 49.984
2019-11-14 | 5:36 | 49.986
2019-11-14 | 5:36 | 49.984
2019-11-14 | 5:36 | 49.984
2019-11-14 | 5:36 | 49.984
2019-11-14 | 5:36 | 49.985
2019-11-14 | 5:36 | 49.986
2019-11-14 | 5:36 | 49.986
2019-11-14 | 5:36 | 49.988
2019-11-14 | 5:36 | 49.99
2019-11-14 | 5:36 | 49.993
2019-11-14 | 5:36 | 49.995
2019-11-14 | 5:36 | 49.998
2019-11-14 | 5:37 | 49.999
2019-11-14 | 5:37 | 50.001
2019-11-14 | 5:37 | 50.005
2019-11-14 | 5:37 | 50.006
2019-11-14 | 5:37 | 50.009
2019-11-14 | 5:37 | 50.012
2019-11-14 | 5:37 | 50.015
2019-11-14 | 5:37 | 50.014
2019-11-14 | 5:37 | 50.016
2019-11-14 | 5:37 | 50.014
2019-11-14 | 5:37 | 50.014
2019-11-14 | 5:37 | 50.012
2019-11-14 | 5:37 | 50.009
2019-11-14 | 5:37 | 50.009
2019-11-14 | 5:37 | 50.007
2019-11-14 | 5:37 | 50.008
2019-11-14 | 5:37 | 50.008
2019-11-14 | 5:37 | 50.007
2019-11-14 | 5:37 | 50.005
2019-11-14 | 5:37 | 50.006
2019-11-14 | 5:37 | 50.006
2019-11-14 | 5:37 | 50.006
2019-11-14 | 5:37 | 50.006
2019-11-14 | 5:37 | 50.006
2019-11-14 | 5:37 | 50.004
2019-11-14 | 5:37 | 50.005
2019-11-14 | 5:37 | 50.006
2019-11-14 | 5:37 | 50.009
2019-11-14 | 5:37 | 50.011

## Event 20191124-1
In UTC
Date | Time | Freq
2019-11-24 | 15:21 | 50.107
2019-11-24 | 15:21 | 50.106
2019-11-24 | 15:21 | 50.109
2019-11-24 | 15:21 | 50.108
2019-11-24 | 15:21 | 50.109
2019-11-24 | 15:21 | 50.109
2019-11-24 | 15:21 | 50.109
2019-11-24 | 15:21 | 50.108
2019-11-24 | 15:21 | 50.11
2019-11-24 | 15:21 | 50.111
2019-11-24 | 15:21 | 50.111
2019-11-24 | 15:21 | 50.111
2019-11-24 | 15:21 | 50.112
2019-11-24 | 15:21 | 50.111
2019-11-24 | 15:21 | 50.114
2019-11-24 | 15:21 | 50.113
2019-11-24 | 15:21 | 50.117
2019-11-24 | 15:21 | 50.117
2019-11-24 | 15:21 | 50.117
2019-11-24 | 15:21 | 50.116
2019-11-24 | 15:21 | 50.117
2019-11-24 | 15:21 | 50.117
2019-11-24 | 15:21 | 50.12
2019-11-24 | 15:21 | 50.121
2019-11-24 | 15:21 | 50.122
2019-11-24 | 15:21 | 50.121
2019-11-24 | 15:21 | 50.123
2019-11-24 | 15:21 | 50.122
2019-11-24 | 15:21 | 50.124
2019-11-24 | 15:21 | 50.124
2019-11-24 | 15:22 | 50.125
2019-11-24 | 15:22 | 50.125
2019-11-24 | 15:22 | 50.125
2019-11-24 | 15:22 | 50.126
2019-11-24 | 15:22 | 50.124
2019-11-24 | 15:22 | 50.125
2019-11-24 | 15:22 | 50.124
2019-11-24 | 15:22 | 50.121
2019-11-24 | 15:22 | 50.121
2019-11-24 | 15:22 | 50.119
2019-11-24 | 15:22 | 50.118
2019-11-24 | 15:22 | 50.118
2019-11-24 | 15:22 | 50.115
2019-11-24 | 15:22 | 50.114
2019-11-24 | 15:22 | 50.113
2019-11-24 | 15:22 | 50.115
2019-11-24 | 15:22 | 50.115
2019-11-24 | 15:22 | 50.116
2019-11-24 | 15:22 | 50.118
2019-11-24 | 15:22 | 50.119
2019-11-24 | 15:22 | 50.122
2019-11-24 | 15:22 | 50.122
2019-11-24 | 15:22 | 50.122
2019-11-24 | 15:22 | 50.122
2019-11-24 | 15:22 | 50.12
2019-11-24 | 15:22 | 50.12
2019-11-24 | 15:22 | 50.118
2019-11-24 | 15:22 | 50.117
2019-11-24 | 15:22 | 50.115
2019-11-24 | 15:22 | 50.114
2019-11-24 | 15:22 | 50.11
2019-11-24 | 15:22 | 50.109
2019-11-24 | 15:22 | 50.107
2019-11-24 | 15:22 | 50.108
2019-11-24 | 15:22 | 50.107
2019-11-24 | 15:22 | 50.107
2019-11-24 | 15:22 | 50.107
2019-11-24 | 15:22 | 50.106
2019-11-24 | 15:22 | 50.106
2019-11-24 | 15:22 | 50.106
2019-11-24 | 15:22 | 50.104
2019-11-24 | 15:22 | 50.103
2019-11-24 | 15:22 | 50.101
2019-11-24 | 15:22 | 50.101
2019-11-24 | 15:22 | 50.1
2019-11-24 | 15:22 | 50.099
2019-11-24 | 15:22 | 50.1
2019-11-24 | 15:22 | 50.101
2019-11-24 | 15:22 | 50.106
2019-11-24 | 15:22 | 50.106
2019-11-24 | 15:22 | 50.109
2019-11-24 | 15:22 | 50.108
2019-11-24 | 15:22 | 50.107
2019-11-24 | 15:22 | 50.104
2019-11-24 | 15:22 | 50.101
2019-11-24 | 15:22 | 50.101
2019-11-24 | 15:22 | 50.101
2019-11-24 | 15:22 | 50.103
2019-11-24 | 15:22 | 50.101
2019-11-24 | 15:22 | 50.1
2019-11-24 | 15:22 | 50.099
2019-11-24 | 15:23 | 50.098
2019-11-24 | 15:23 | 50.097
2019-11-24 | 15:23 | 50.094
2019-11-24 | 15:23 | 50.092
2019-11-24 | 15:23 | 50.087
2019-11-24 | 15:23 | 50.088
2019-11-24 | 15:23 | 50.086
2019-11-24 | 15:23 | 50.087
2019-11-24 | 15:23 | 50.087
2019-11-24 | 15:23 | 50.088
2019-11-24 | 15:23 | 50.088
2019-11-24 | 15:23 | 50.087
2019-11-24 | 15:23 | 50.086
2019-11-24 | 15:23 | 50.087
2019-11-24 | 15:23 | 50.087
2019-11-24 | 15:23 | 50.082
2019-11-24 | 15:23 | 50.084
2019-11-24 | 15:23 | 50.082
2019-11-24 | 15:23 | 50.082
2019-11-24 | 15:23 | 50.08
2019-11-24 | 15:23 | 50.08
2019-11-24 | 15:23 | 50.078
2019-11-24 | 15:23 | 50.078
2019-11-24 | 15:23 | 50.077
2019-11-24 | 15:23 | 50.078
2019-11-24 | 15:23 | 50.079
2019-11-24 | 15:23 | 50.079
2019-11-24 | 15:23 | 50.082
2019-11-24 | 15:23 | 50.085
2019-11-24 | 15:23 | 50.087
2019-11-24 | 15:23 | 50.088
2019-11-24 | 15:23 | 50.09
2019-11-24 | 15:23 | 50.092
2019-11-24 | 15:23 | 50.092
2019-11-24 | 15:23 | 50.092
2019-11-24 | 15:23 | 50.093
2019-11-24 | 15:23 | 50.092
2019-11-24 | 15:23 | 50.094
2019-11-24 | 15:23 | 50.093
2019-11-24 | 15:23 | 50.092
2019-11-24 | 15:23 | 50.09
2019-11-24 | 15:23 | 50.091
2019-11-24 | 15:23 | 50.09
2019-11-24 | 15:23 | 50.09
2019-11-24 | 15:23 | 50.092
2019-11-24 | 15:23 | 50.092
2019-11-24 | 15:23 | 50.095
2019-11-24 | 15:23 | 50.096
2019-11-24 | 15:23 | 50.1
2019-11-24 | 15:23 | 50.099
2019-11-24 | 15:23 | 50.1
2019-11-24 | 15:23 | 50.099
2019-11-24 | 15:23 | 50.1
2019-11-24 | 15:23 | 50.1
2019-11-24 | 15:23 | 50.1
2019-11-24 | 15:23 | 50.098
2019-11-24 | 15:23 | 50.097
2019-11-24 | 15:23 | 50.096
2019-11-24 | 15:23 | 50.095
2019-11-24 | 15:24 | 50.094
2019-11-24 | 15:24 | 50.091
2019-11-24 | 15:24 | 50.093
2019-11-24 | 15:24 | 50.09
2019-11-24 | 15:24 | 50.088
2019-11-24 | 15:24 | 50.084
2019-11-24 | 15:24 | 50.082
2019-11-24 | 15:24 | 50.079
2019-11-24 | 15:24 | 50.077
2019-11-24 | 15:24 | 50.077
2019-11-24 | 15:24 | 50.077
2019-11-24 | 15:24 | 50.076
2019-11-24 | 15:24 | 50.076
2019-11-24 | 15:24 | 50.075
2019-11-24 | 15:24 | 50.075
2019-11-24 | 15:24 | 50.073
2019-11-24 | 15:24 | 50.074
2019-11-24 | 15:24 | 50.074
2019-11-24 | 15:24 | 50.073
2019-11-24 | 15:24 | 50.072
2019-11-24 | 15:24 | 50.072
2019-11-24 | 15:24 | 50.071
2019-11-24 | 15:24 | 50.072
2019-11-24 | 15:24 | 50.072
2019-11-24 | 15:24 | 50.073
2019-11-24 | 15:24 | 50.072
2019-11-24 | 15:24 | 50.073
2019-11-24 | 15:24 | 50.072
2019-11-24 | 15:24 | 50.072
2019-11-24 | 15:24 | 50.072
2019-11-24 | 15:24 | 50.072
2019-11-24 | 15:24 | 50.069
2019-11-24 | 15:24 | 50.065
2019-11-24 | 15:24 | 50.063
2019-11-24 | 15:24 | 50.06
2019-11-24 | 15:24 | 50.058
2019-11-24 | 15:24 | 50.058
2019-11-24 | 15:24 | 50.059
2019-11-24 | 15:24 | 50.058
2019-11-24 | 15:24 | 50.06
2019-11-24 | 15:24 | 50.058
2019-11-24 | 15:24 | 50.059
2019-11-24 | 15:24 | 50.056
2019-11-24 | 15:24 | 50.055
2019-11-24 | 15:24 | 50.054
2019-11-24 | 15:24 | 50.052
2019-11-24 | 15:24 | 50.051
2019-11-24 | 15:24 | 50.054
2019-11-24 | 15:24 | 50.058
2019-11-24 | 15:24 | 50.059
2019-11-24 | 15:24 | 50.062
2019-11-24 | 15:24 | 50.064
2019-11-24 | 15:24 | 50.066
2019-11-24 | 15:24 | 50.066
2019-11-24 | 15:24 | 50.066
2019-11-24 | 15:24 | 50.065
2019-11-24 | 15:24 | 50.063
2019-11-24 | 15:24 | 50.062
2019-11-24 | 15:24 | 50.065
2019-11-24 | 15:24 | 50.068
2019-11-24 | 15:24 | 50.071
2019-11-24 | 15:25 | 50.074
2019-11-24 | 15:25 | 50.078
2019-11-24 | 15:25 | 50.08
2019-11-24 | 15:25 | 50.081
2019-11-24 | 15:25 | 50.084
2019-11-24 | 15:25 | 50.081
2019-11-24 | 15:25 | 50.081
2019-11-24 | 15:25 | 50.08
2019-11-24 | 15:25 | 50.08
2019-11-24 | 15:25 | 50.076
2019-11-24 | 15:25 | 50.075
2019-11-24 | 15:25 | 50.074
2019-11-24 | 15:25 | 50.074
2019-11-24 | 15:25 | 50.074
2019-11-24 | 15:25 | 50.077
2019-11-24 | 15:25 | 50.078
2019-11-24 | 15:25 | 50.083
2019-11-24 | 15:25 | 50.084
2019-11-24 | 15:25 | 50.085
2019-11-24 | 15:25 | 50.087
2019-11-24 | 15:25 | 50.088
2019-11-24 | 15:25 | 50.09
2019-11-24 | 15:25 | 50.09
2019-11-24 | 15:25 | 50.09
2019-11-24 | 15:25 | 50.088
2019-11-24 | 15:25 | 50.086
2019-11-24 | 15:25 | 50.086
2019-11-24 | 15:25 | 50.082
2019-11-24 | 15:25 | 50.08
2019-11-24 | 15:25 | 50.077
2019-11-24 | 15:25 | 50.076
2019-11-24 | 15:25 | 50.073
2019-11-24 | 15:25 | 50.072
2019-11-24 | 15:25 | 50.071
2019-11-24 | 15:25 | 50.07
2019-11-24 | 15:25 | 50.07
2019-11-24 | 15:25 | 50.069
2019-11-24 | 15:25 | 50.071
2019-11-24 | 15:25 | 50.069
2019-11-24 | 15:25 | 50.068
2019-11-24 | 15:25 | 50.067
2019-11-24 | 15:25 | 50.069
2019-11-24 | 15:25 | 50.07
2019-11-24 | 15:25 | 50.072
2019-11-24 | 15:25 | 50.075
2019-11-24 | 15:25 | 50.077
2019-11-24 | 15:25 | 50.079
2019-11-24 | 15:25 | 50.082
2019-11-24 | 15:25 | 50.082
2019-11-24 | 15:25 | 50.082
2019-11-24 | 15:25 | 50.08
2019-11-24 | 15:25 | 50.079
2019-11-24 | 15:25 | 50.077
2019-11-24 | 15:25 | 50.075
2019-11-24 | 15:25 | 50.074
2019-11-24 | 15:25 | 50.072
2019-11-24 | 15:25 | 50.074
2019-11-24 | 15:25 | 50.072
2019-11-24 | 15:25 | 50.075
2019-11-24 | 15:26 | 50.074
2019-11-24 | 15:26 | 50.076
2019-11-24 | 15:26 | 50.075
2019-11-24 | 15:26 | 50.078
2019-11-24 | 15:26 | 50.076
2019-11-24 | 15:26 | 50.076
2019-11-24 | 15:26 | 50.077
2019-11-24 | 15:26 | 50.078
2019-11-24 | 15:26 | 50.079
2019-11-24 | 15:26 | 50.078
2019-11-24 | 15:26 | 50.08
2019-11-24 | 15:26 | 50.08
2019-11-24 | 15:26 | 50.079
2019-11-24 | 15:26 | 50.078
2019-11-24 | 15:26 | 50.078
2019-11-24 | 15:26 | 50.075
2019-11-24 | 15:26 | 50.075
2019-11-24 | 15:26 | 50.07
2019-11-24 | 15:26 | 50.069
2019-11-24 | 15:26 | 50.065
2019-11-24 | 15:26 | 50.062
2019-11-24 | 15:26 | 50.06
2019-11-24 | 15:26 | 50.059
2019-11-24 | 15:26 | 50.057
2019-11-24 | 15:26 | 50.055
2019-11-24 | 15:26 | 50.055
2019-11-24 | 15:26 | 50.051
2019-11-24 | 15:26 | 50.051
2019-11-24 | 15:26 | 50.047
2019-11-24 | 15:26 | 50.044
2019-11-24 | 15:26 | 50.04
2019-11-24 | 15:26 | 50.044
2019-11-24 | 15:26 | 50.045
2019-11-24 | 15:26 | 50.05
2019-11-24 | 15:26 | 50.053
2019-11-24 | 15:26 | 50.056
2019-11-24 | 15:26 | 50.058
2019-11-24 | 15:26 | 50.061
2019-11-24 | 15:26 | 50.062
2019-11-24 | 15:26 | 50.064
2019-11-24 | 15:26 | 50.06
2019-11-24 | 15:26 | 50.058
2019-11-24 | 15:26 | 50.059
2019-11-24 | 15:26 | 50.059
2019-11-24 | 15:26 | 50.061
2019-11-24 | 15:26 | 50.062
2019-11-24 | 15:26 | 50.066
2019-11-24 | 15:26 | 50.067
2019-11-24 | 15:26 | 50.069
2019-11-24 | 15:26 | 50.069
2019-11-24 | 15:26 | 50.07
2019-11-24 | 15:26 | 50.072
2019-11-24 | 15:26 | 50.07
2019-11-24 | 15:26 | 50.07
2019-11-24 | 15:26 | 50.07
2019-11-24 | 15:26 | 50.07
2019-11-24 | 15:26 | 50.069
2019-11-24 | 15:26 | 50.072
2019-11-24 | 15:26 | 50.071
2019-11-24 | 15:26 | 50.074
2019-11-24 | 15:26 | 50.075
2019-11-24 | 15:27 | 50.077
2019-11-24 | 15:27 | 50.079
2019-11-24 | 15:27 | 50.08
2019-11-24 | 15:27 | 50.083
2019-11-24 | 15:27 | 50.086
2019-11-24 | 15:27 | 50.088
2019-11-24 | 15:27 | 50.09
2019-11-24 | 15:27 | 50.093
2019-11-24 | 15:27 | 50.094
2019-11-24 | 15:27 | 50.096
2019-11-24 | 15:27 | 50.098
2019-11-24 | 15:27 | 50.102
2019-11-24 | 15:27 | 50.105
2019-11-24 | 15:27 | 50.107
2019-11-24 | 15:27 | 50.108
2019-11-24 | 15:27 | 50.109
2019-11-24 | 15:27 | 50.11
2019-11-24 | 15:27 | 50.107
2019-11-24 | 15:27 | 50.107
2019-11-24 | 15:27 | 50.107
2019-11-24 | 15:27 | 50.105
2019-11-24 | 15:27 | 50.103
2019-11-24 | 15:27 | 50.102
2019-11-24 | 15:27 | 50.1
2019-11-24 | 15:27 | 50.096
2019-11-24 | 15:27 | 50.094
2019-11-24 | 15:27 | 50.092
2019-11-24 | 15:27 | 50.088
2019-11-24 | 15:27 | 50.086
2019-11-24 | 15:27 | 50.082
2019-11-24 | 15:27 | 50.082
2019-11-24 | 15:27 | 50.083
2019-11-24 | 15:27 | 50.083
2019-11-24 | 15:27 | 50.083
2019-11-24 | 15:27 | 50.084
2019-11-24 | 15:27 | 50.087
2019-11-24 | 15:27 | 50.089
2019-11-24 | 15:27 | 50.089
2019-11-24 | 15:27 | 50.09
2019-11-24 | 15:27 | 50.093
2019-11-24 | 15:27 | 50.092
2019-11-24 | 15:27 | 50.095
2019-11-24 | 15:27 | 50.094
2019-11-24 | 15:27 | 50.094
2019-11-24 | 15:27 | 50.093
2019-11-24 | 15:27 | 50.091
2019-11-24 | 15:27 | 50.09
2019-11-24 | 15:27 | 50.088
2019-11-24 | 15:27 | 50.084
2019-11-24 | 15:27 | 50.082
2019-11-24 | 15:27 | 50.081
2019-11-24 | 15:27 | 50.079
2019-11-24 | 15:27 | 50.079
2019-11-24 | 15:27 | 50.077
2019-11-24 | 15:27 | 50.078
2019-11-24 | 15:27 | 50.076
2019-11-24 | 15:27 | 50.08
2019-11-24 | 15:27 | 50.079
2019-11-24 | 15:27 | 50.081
2019-11-24 | 15:28 | 50.082
2019-11-24 | 15:28 | 50.082
2019-11-24 | 15:28 | 50.083
2019-11-24 | 15:28 | 50.085
2019-11-24 | 15:28 | 50.084
2019-11-24 | 15:28 | 50.085
2019-11-24 | 15:28 | 50.084
2019-11-24 | 15:28 | 50.083
2019-11-24 | 15:28 | 50.082
2019-11-24 | 15:28 | 50.084
2019-11-24 | 15:28 | 50.081
2019-11-24 | 15:28 | 50.082
2019-11-24 | 15:28 | 50.081
2019-11-24 | 15:28 | 50.083
2019-11-24 | 15:28 | 50.085
2019-11-24 | 15:28 | 50.086
2019-11-24 | 15:28 | 50.09
2019-11-24 | 15:28 | 50.091
2019-11-24 | 15:28 | 50.094
2019-11-24 | 15:28 | 50.094
2019-11-24 | 15:28 | 50.096
2019-11-24 | 15:28 | 50.093
2019-11-24 | 15:28 | 50.092
2019-11-24 | 15:28 | 50.088
2019-11-24 | 15:28 | 50.087
2019-11-24 | 15:28 | 50.086
2019-11-24 | 15:28 | 50.084
2019-11-24 | 15:28 | 50.085
2019-11-24 | 15:28 | 50.086
2019-11-24 | 15:28 | 50.086
2019-11-24 | 15:28 | 50.087
2019-11-24 | 15:28 | 50.09
2019-11-24 | 15:28 | 50.09
2019-11-24 | 15:28 | 50.088
2019-11-24 | 15:28 | 50.088
2019-11-24 | 15:28 | 50.087
2019-11-24 | 15:28 | 50.091
2019-11-24 | 15:28 | 50.093
2019-11-24 | 15:28 | 50.098
2019-11-24 | 15:28 | 50.1
2019-11-24 | 15:28 | 50.103
2019-11-24 | 15:28 | 50.104
2019-11-24 | 15:28 | 50.104
2019-11-24 | 15:28 | 50.103
2019-11-24 | 15:28 | 50.102
2019-11-24 | 15:28 | 50.1
2019-11-24 | 15:28 | 50.097
2019-11-24 | 15:28 | 50.094
2019-11-24 | 15:28 | 50.091
2019-11-24 | 15:28 | 50.09
2019-11-24 | 15:28 | 50.086
2019-11-24 | 15:28 | 50.083
2019-11-24 | 15:28 | 50.081
2019-11-24 | 15:28 | 50.079
2019-11-24 | 15:28 | 50.077
2019-11-24 | 15:28 | 50.077
2019-11-24 | 15:28 | 50.077
2019-11-24 | 15:28 | 50.077
2019-11-24 | 15:28 | 50.079
2019-11-24 | 15:28 | 50.082
2019-11-24 | 15:28 | 50.084
2019-11-24 | 15:29 | 50.086
2019-11-24 | 15:29 | 50.086
2019-11-24 | 15:29 | 50.088
2019-11-24 | 15:29 | 50.089
2019-11-24 | 15:29 | 50.093
2019-11-24 | 15:29 | 50.093
2019-11-24 | 15:29 | 50.095
2019-11-24 | 15:29 | 50.095
2019-11-24 | 15:29 | 50.095
2019-11-24 | 15:29 | 50.095
2019-11-24 | 15:29 | 50.094
2019-11-24 | 15:29 | 50.094
2019-11-24 | 15:29 | 50.093
2019-11-24 | 15:29 | 50.096
2019-11-24 | 15:29 | 50.096
2019-11-24 | 15:29 | 50.096
2019-11-24 | 15:29 | 50.095
2019-11-24 | 15:29 | 50.095
2019-11-24 | 15:29 | 50.095
2019-11-24 | 15:29 | 50.096
2019-11-24 | 15:29 | 50.096
2019-11-24 | 15:29 | 50.097
2019-11-24 | 15:29 | 50.099
2019-11-24 | 15:29 | 50.1
2019-11-24 | 15:29 | 50.1
2019-11-24 | 15:29 | 50.101
2019-11-24 | 15:29 | 50.101
2019-11-24 | 15:29 | 50.1
2019-11-24 | 15:29 | 50.1
2019-11-24 | 15:29 | 50.097
2019-11-24 | 15:29 | 50.098
2019-11-24 | 15:29 | 50.097
2019-11-24 | 15:29 | 50.096
2019-11-24 | 15:29 | 50.094
2019-11-24 | 15:29 | 50.094
2019-11-24 | 15:29 | 50.092
2019-11-24 | 15:29 | 50.092
2019-11-24 | 15:29 | 50.089
2019-11-24 | 15:29 | 50.091
2019-11-24 | 15:29 | 50.09
2019-11-24 | 15:29 | 50.09
2019-11-24 | 15:29 | 50.087
2019-11-24 | 15:29 | 50.087
2019-11-24 | 15:29 | 50.083
2019-11-24 | 15:29 | 50.082
2019-11-24 | 15:29 | 50.076
2019-11-24 | 15:29 | 50.075
2019-11-24 | 15:29 | 50.071
2019-11-24 | 15:29 | 50.069
2019-11-24 | 15:29 | 50.067
2019-11-24 | 15:29 | 50.066
2019-11-24 | 15:29 | 50.065
2019-11-24 | 15:29 | 50.066
2019-11-24 | 15:29 | 50.065
2019-11-24 | 15:29 | 50.066
2019-11-24 | 15:29 | 50.065
2019-11-24 | 15:29 | 50.066
2019-11-24 | 15:29 | 50.065
2019-11-24 | 15:29 | 50.066
2019-11-24 | 15:30 | 50.065
2019-11-24 | 15:30 | 50.065
2019-11-24 | 15:30 | 50.065
2019-11-24 | 15:30 | 50.064
2019-11-24 | 15:30 | 50.063
2019-11-24 | 15:30 | 50.065
2019-11-24 | 15:30 | 50.065
2019-11-24 | 15:30 | 50.068
2019-11-24 | 15:30 | 50.068
2019-11-24 | 15:30 | 50.07
2019-11-24 | 15:30 | 50.07
2019-11-24 | 15:30 | 50.073
2019-11-24 | 15:30 | 50.071
2019-11-24 | 15:30 | 50.069
2019-11-24 | 15:30 | 50.068
2019-11-24 | 15:30 | 50.068
2019-11-24 | 15:30 | 50.068
2019-11-24 | 15:30 | 50.072
2019-11-24 | 15:30 | 50.071
2019-11-24 | 15:30 | 50.073
2019-11-24 | 15:30 | 50.072
2019-11-24 | 15:30 | 50.075
2019-11-24 | 15:30 | 50.074
2019-11-24 | 15:30 | 50.075
2019-11-24 | 15:30 | 50.075
2019-11-24 | 15:30 | 50.076
2019-11-24 | 15:30 | 50.076
2019-11-24 | 15:30 | 50.078
2019-11-24 | 15:30 | 50.079
2019-11-24 | 15:30 | 50.081
2019-11-24 | 15:30 | 50.082
2019-11-24 | 15:30 | 50.085
2019-11-24 | 15:30 | 50.086
2019-11-24 | 15:30 | 50.088
2019-11-24 | 15:30 | 50.09
2019-11-24 | 15:30 | 50.092
2019-11-24 | 15:30 | 50.093
2019-11-24 | 15:30 | 50.093
2019-11-24 | 15:30 | 50.093
2019-11-24 | 15:30 | 50.092
2019-11-24 | 15:30 | 50.093
2019-11-24 | 15:30 | 50.093
2019-11-24 | 15:30 | 50.094
2019-11-24 | 15:30 | 50.096
2019-11-24 | 15:30 | 50.097
2019-11-24 | 15:30 | 50.099
2019-11-24 | 15:30 | 50.1
2019-11-24 | 15:30 | 50.102
2019-11-24 | 15:30 | 50.103
2019-11-24 | 15:30 | 50.105
2019-11-24 | 15:30 | 50.107
2019-11-24 | 15:30 | 50.108
2019-11-24 | 15:30 | 50.11
2019-11-24 | 15:30 | 50.112
2019-11-24 | 15:30 | 50.114
2019-11-24 | 15:30 | 50.117
2019-11-24 | 15:30 | 50.117
2019-11-24 | 15:30 | 50.119
2019-11-24 | 15:30 | 50.12
2019-11-24 | 15:30 | 50.122
2019-11-24 | 15:30 | 50.123
2019-11-24 | 15:31 | 50.126
2019-11-24 | 15:31 | 50.126
2019-11-24 | 15:31 | 50.125
2019-11-24 | 15:31 | 50.122
2019-11-24 | 15:31 | 50.119
2019-11-24 | 15:31 | 50.119
2019-11-24 | 15:31 | 50.118
2019-11-24 | 15:31 | 50.117
2019-11-24 | 15:31 | 50.114
2019-11-24 | 15:31 | 50.114
2019-11-24 | 15:31 | 50.112
2019-11-24 | 15:31 | 50.112
2019-11-24 | 15:31 | 50.111
2019-11-24 | 15:31 | 50.111
2019-11-24 | 15:31 | 50.112
2019-11-24 | 15:31 | 50.111
2019-11-24 | 15:31 | 50.113
2019-11-24 | 15:31 | 50.115
2019-11-24 | 15:31 | 50.119
2019-11-24 | 15:31 | 50.119
2019-11-24 | 15:31 | 50.122
2019-11-24 | 15:31 | 50.124
2019-11-24 | 15:31 | 50.126
2019-11-24 | 15:31 | 50.127
2019-11-24 | 15:31 | 50.127
2019-11-24 | 15:31 | 50.128
2019-11-24 | 15:31 | 50.13
2019-11-24 | 15:31 | 50.13
2019-11-24 | 15:31 | 50.131
2019-11-24 | 15:31 | 50.132
2019-11-24 | 15:31 | 50.132
2019-11-24 | 15:31 | 50.132
2019-11-24 | 15:31 | 50.133
2019-11-24 | 15:31 | 50.132
2019-11-24 | 15:31 | 50.13
2019-11-24 | 15:31 | 50.13
2019-11-24 | 15:31 | 50.131
2019-11-24 | 15:31 | 50.129
2019-11-24 | 15:31 | 50.13
2019-11-24 | 15:31 | 50.132
2019-11-24 | 15:31 | 50.135
2019-11-24 | 15:31 | 50.137
2019-11-24 | 15:31 | 50.138
2019-11-24 | 15:31 | 50.139
2019-11-24 | 15:31 | 50.138
2019-11-24 | 15:31 | 50.138
2019-11-24 | 15:31 | 50.136
2019-11-24 | 15:31 | 50.135
2019-11-24 | 15:31 | 50.135
2019-11-24 | 15:31 | 50.134
2019-11-24 | 15:31 | 50.133
2019-11-24 | 15:31 | 50.13
2019-11-24 | 15:31 | 50.128
2019-11-24 | 15:31 | 50.124
2019-11-24 | 15:31 | 50.121
2019-11-24 | 15:31 | 50.118
2019-11-24 | 15:31 | 50.117
2019-11-24 | 15:31 | 50.113
2019-11-24 | 15:31 | 50.111
2019-11-24 | 15:32 | 50.109
2019-11-24 | 15:32 | 50.109
2019-11-24 | 15:32 | 50.106
2019-11-24 | 15:32 | 50.106
2019-11-24 | 15:32 | 50.104
2019-11-24 | 15:32 | 50.102
2019-11-24 | 15:32 | 50.1
2019-11-24 | 15:32 | 50.1
2019-11-24 | 15:32 | 50.101
2019-11-24 | 15:32 | 50.103
2019-11-24 | 15:32 | 50.103
2019-11-24 | 15:32 | 50.106
2019-11-24 | 15:32 | 50.108
2019-11-24 | 15:32 | 50.108
2019-11-24 | 15:32 | 50.111
2019-11-24 | 15:32 | 50.111
2019-11-24 | 15:32 | 50.111
2019-11-24 | 15:32 | 50.109
2019-11-24 | 15:32 | 50.11
2019-11-24 | 15:32 | 50.109
2019-11-24 | 15:32 | 50.111
2019-11-24 | 15:32 | 50.109
2019-11-24 | 15:32 | 50.11
2019-11-24 | 15:32 | 50.112
2019-11-24 | 15:32 | 50.115
2019-11-24 | 15:32 | 50.117
2019-11-24 | 15:32 | 50.119
2019-11-24 | 15:32 | 50.121
2019-11-24 | 15:32 | 50.124
2019-11-24 | 15:32 | 50.122
2019-11-24 | 15:32 | 50.122
2019-11-24 | 15:32 | 50.121
2019-11-24 | 15:32 | 50.12
2019-11-24 | 15:32 | 50.12
2019-11-24 | 15:32 | 50.119
2019-11-24 | 15:32 | 50.123
2019-11-24 | 15:32 | 50.122
2019-11-24 | 15:32 | 50.125
2019-11-24 | 15:32 | 50.129
2019-11-24 | 15:32 | 50.133
2019-11-24 | 15:32 | 50.133
2019-11-24 | 15:32 | 50.133
2019-11-24 | 15:32 | 50.135
2019-11-24 | 15:32 | 50.132
2019-11-24 | 15:32 | 50.131
2019-11-24 | 15:32 | 50.133
2019-11-24 | 15:32 | 50.131
2019-11-24 | 15:32 | 50.134
2019-11-24 | 15:32 | 50.133
2019-11-24 | 15:32 | 50.137
2019-11-24 | 15:32 | 50.136
2019-11-24 | 15:32 | 50.139
2019-11-24 | 15:32 | 50.139
2019-11-24 | 15:32 | 50.142
2019-11-24 | 15:32 | 50.142
2019-11-24 | 15:32 | 50.143
2019-11-24 | 15:32 | 50.143
2019-11-24 | 15:32 | 50.144
2019-11-24 | 15:32 | 50.144
2019-11-24 | 15:32 | 50.145
2019-11-24 | 15:32 | 50.144
2019-11-24 | 15:33 | 50.145
2019-11-24 | 15:33 | 50.142
2019-11-24 | 15:33 | 50.144
2019-11-24 | 15:33 | 50.141
2019-11-24 | 15:33 | 50.142
2019-11-24 | 15:33 | 50.139
2019-11-24 | 15:33 | 50.136
2019-11-24 | 15:33 | 50.136
2019-11-24 | 15:33 | 50.131
2019-11-24 | 15:33 | 50.128
2019-11-24 | 15:33 | 50.125
2019-11-24 | 15:33 | 50.123
2019-11-24 | 15:33 | 50.124
2019-11-24 | 15:33 | 50.122
2019-11-24 | 15:33 | 50.12
2019-11-24 | 15:33 | 50.121
2019-11-24 | 15:33 | 50.119
2019-11-24 | 15:33 | 50.12
2019-11-24 | 15:33 | 50.118
2019-11-24 | 15:33 | 50.118
2019-11-24 | 15:33 | 50.118
2019-11-24 | 15:33 | 50.118
2019-11-24 | 15:33 | 50.118
2019-11-24 | 15:33 | 50.118
2019-11-24 | 15:33 | 50.116
2019-11-24 | 15:33 | 50.115
2019-11-24 | 15:33 | 50.113
2019-11-24 | 15:33 | 50.112
2019-11-24 | 15:33 | 50.111
2019-11-24 | 15:33 | 50.109
2019-11-24 | 15:33 | 50.108
2019-11-24 | 15:33 | 50.104
2019-11-24 | 15:33 | 50.102
2019-11-24 | 15:33 | 50.096
2019-11-24 | 15:33 | 50.094
2019-11-24 | 15:33 | 50.092
2019-11-24 | 15:33 | 50.091
2019-11-24 | 15:33 | 50.09
2019-11-24 | 15:33 | 50.088
2019-11-24 | 15:33 | 50.087
2019-11-24 | 15:33 | 50.088
2019-11-24 | 15:33 | 50.088
2019-11-24 | 15:33 | 50.089
2019-11-24 | 15:33 | 50.091
2019-11-24 | 15:33 | 50.095
2019-11-24 | 15:33 | 50.096
2019-11-24 | 15:33 | 50.099
2019-11-24 | 15:33 | 50.103
2019-11-24 | 15:33 | 50.105
2019-11-24 | 15:33 | 50.103
2019-11-24 | 15:33 | 50.104
2019-11-24 | 15:33 | 50.101
2019-11-24 | 15:33 | 50.1
2019-11-24 | 15:33 | 50.1
2019-11-24 | 15:33 | 50.102
2019-11-24 | 15:33 | 50.102
2019-11-24 | 15:33 | 50.101
2019-11-24 | 15:33 | 50.102
2019-11-24 | 15:33 | 50.102
2019-11-24 | 15:34 | 50.103
2019-11-24 | 15:34 | 50.104
2019-11-24 | 15:34 | 50.104
2019-11-24 | 15:34 | 50.102
2019-11-24 | 15:34 | 50.102
2019-11-24 | 15:34 | 50.101
2019-11-24 | 15:34 | 50.1
2019-11-24 | 15:34 | 50.103
2019-11-24 | 15:34 | 50.103
2019-11-24 | 15:34 | 50.105
2019-11-24 | 15:34 | 50.103
2019-11-24 | 15:34 | 50.104
2019-11-24 | 15:34 | 50.103
2019-11-24 | 15:34 | 50.102
2019-11-24 | 15:34 | 50.103
2019-11-24 | 15:34 | 50.102
2019-11-24 | 15:34 | 50.101
2019-11-24 | 15:34 | 50.099
2019-11-24 | 15:34 | 50.1
2019-11-24 | 15:34 | 50.097
2019-11-24 | 15:34 | 50.095
2019-11-24 | 15:34 | 50.095
2019-11-24 | 15:34 | 50.091
2019-11-24 | 15:34 | 50.092
2019-11-24 | 15:34 | 50.091
2019-11-24 | 15:34 | 50.091
2019-11-24 | 15:34 | 50.092
2019-11-24 | 15:34 | 50.091
2019-11-24 | 15:34 | 50.094
2019-11-24 | 15:34 | 50.092
2019-11-24 | 15:34 | 50.092
2019-11-24 | 15:34 | 50.091
2019-11-24 | 15:34 | 50.091
2019-11-24 | 15:34 | 50.088
2019-11-24 | 15:34 | 50.087
2019-11-24 | 15:34 | 50.088
2019-11-24 | 15:34 | 50.089
2019-11-24 | 15:34 | 50.089
2019-11-24 | 15:34 | 50.088
2019-11-24 | 15:34 | 50.09
2019-11-24 | 15:34 | 50.088
2019-11-24 | 15:34 | 50.088
2019-11-24 | 15:34 | 50.085
2019-11-24 | 15:34 | 50.084
2019-11-24 | 15:34 | 50.084
2019-11-24 | 15:34 | 50.085
2019-11-24 | 15:34 | 50.085
2019-11-24 | 15:34 | 50.086
2019-11-24 | 15:34 | 50.087
2019-11-24 | 15:34 | 50.087
2019-11-24 | 15:34 | 50.089
2019-11-24 | 15:34 | 50.092
2019-11-24 | 15:34 | 50.092
2019-11-24 | 15:34 | 50.091
2019-11-24 | 15:34 | 50.092
2019-11-24 | 15:34 | 50.092
2019-11-24 | 15:34 | 50.095
2019-11-24 | 15:34 | 50.095
2019-11-24 | 15:34 | 50.097
2019-11-24 | 15:34 | 50.098
2019-11-24 | 15:34 | 50.098
2019-11-24 | 15:35 | 50.099
2019-11-24 | 15:35 | 50.1
2019-11-24 | 15:35 | 50.1
2019-11-24 | 15:35 | 50.1
2019-11-24 | 15:35 | 50.097
2019-11-24 | 15:35 | 50.097
2019-11-24 | 15:35 | 50.095
2019-11-24 | 15:35 | 50.092
2019-11-24 | 15:35 | 50.089
2019-11-24 | 15:35 | 50.084
2019-11-24 | 15:35 | 50.084
2019-11-24 | 15:35 | 50.083
2019-11-24 | 15:35 | 50.082
2019-11-24 | 15:35 | 50.079
2019-11-24 | 15:35 | 50.078
2019-11-24 | 15:35 | 50.076
2019-11-24 | 15:35 | 50.076
2019-11-24 | 15:35 | 50.073
2019-11-24 | 15:35 | 50.07
2019-11-24 | 15:35 | 50.07
2019-11-24 | 15:35 | 50.067
2019-11-24 | 15:35 | 50.067
2019-11-24 | 15:35 | 50.065
2019-11-24 | 15:35 | 50.066
2019-11-24 | 15:35 | 50.063
2019-11-24 | 15:35 | 50.063
2019-11-24 | 15:35 | 50.062
2019-11-24 | 15:35 | 50.061
2019-11-24 | 15:35 | 50.057
2019-11-24 | 15:35 | 50.059
2019-11-24 | 15:35 | 50.057
2019-11-24 | 15:35 | 50.056
2019-11-24 | 15:35 | 50.054
2019-11-24 | 15:35 | 50.052
2019-11-24 | 15:35 | 50.049
2019-11-24 | 15:35 | 50.05
2019-11-24 | 15:35 | 50.048
2019-11-24 | 15:35 | 50.047
2019-11-24 | 15:35 | 50.045
2019-11-24 | 15:35 | 50.042
2019-11-24 | 15:35 | 50.037
2019-11-24 | 15:35 | 50.035
2019-11-24 | 15:35 | 50.031
2019-11-24 | 15:35 | 50.034
2019-11-24 | 15:35 | 50.032
2019-11-24 | 15:35 | 50.033
2019-11-24 | 15:35 | 50.032
2019-11-24 | 15:35 | 50.032
2019-11-24 | 15:35 | 50.032
2019-11-24 | 15:35 | 50.033
2019-11-24 | 15:35 | 50.03
2019-11-24 | 15:35 | 50.029
2019-11-24 | 15:35 | 50.026
2019-11-24 | 15:35 | 50.026
2019-11-24 | 15:35 | 50.025
2019-11-24 | 15:35 | 50.03
2019-11-24 | 15:35 | 50.032
2019-11-24 | 15:35 | 50.036
2019-11-24 | 15:35 | 50.039
2019-11-24 | 15:36 | 50.043
2019-11-24 | 15:36 | 50.047
2019-11-24 | 15:36 | 50.048
2019-11-24 | 15:36 | 50.049
2019-11-24 | 15:36 | 50.049
2019-11-24 | 15:36 | 50.049
2019-11-24 | 15:36 | 50.046
2019-11-24 | 15:36 | 50.043
2019-11-24 | 15:36 | 50.041
2019-11-24 | 15:36 | 50.041
2019-11-24 | 15:36 | 50.038
2019-11-24 | 15:36 | 50.042
2019-11-24 | 15:36 | 50.04
2019-11-24 | 15:36 | 50.042
2019-11-24 | 15:36 | 50.043
2019-11-24 | 15:36 | 50.046
2019-11-24 | 15:36 | 50.046
2019-11-24 | 15:36 | 50.051
2019-11-24 | 15:36 | 50.053
2019-11-24 | 15:36 | 50.054
2019-11-24 | 15:36 | 50.054
2019-11-24 | 15:36 | 50.055
2019-11-24 | 15:36 | 50.054
2019-11-24 | 15:36 | 50.052
2019-11-24 | 15:36 | 50.05
2019-11-24 | 15:36 | 50.045
2019-11-24 | 15:36 | 50.043
2019-11-24 | 15:36 | 50.041
2019-11-24 | 15:36 | 50.039
2019-11-24 | 15:36 | 50.04
2019-11-24 | 15:36 | 50.038
2019-11-24 | 15:36 | 50.035
2019-11-24 | 15:36 | 50.036
2019-11-24 | 15:36 | 50.038
2019-11-24 | 15:36 | 50.039
2019-11-24 | 15:36 | 50.043
2019-11-24 | 15:36 | 50.044
2019-11-24 | 15:36 | 50.048
2019-11-24 | 15:36 | 50.05
2019-11-24 | 15:36 | 50.053
2019-11-24 | 15:36 | 50.055
2019-11-24 | 15:36 | 50.058
2019-11-24 | 15:36 | 50.059
2019-11-24 | 15:36 | 50.059
2019-11-24 | 15:36 | 50.06
2019-11-24 | 15:36 | 50.061
2019-11-24 | 15:36 | 50.061
2019-11-24 | 15:36 | 50.061
2019-11-24 | 15:36 | 50.062
2019-11-24 | 15:36 | 50.061
2019-11-24 | 15:36 | 50.063
2019-11-24 | 15:36 | 50.061
2019-11-24 | 15:36 | 50.061
2019-11-24 | 15:36 | 50.06
2019-11-24 | 15:36 | 50.06
2019-11-24 | 15:36 | 50.059
2019-11-24 | 15:36 | 50.059
2019-11-24 | 15:36 | 50.061
2019-11-24 | 15:36 | 50.06
2019-11-24 | 15:36 | 50.058
2019-11-24 | 15:36 | 50.057
2019-11-24 | 15:37 | 50.055
2019-11-24 | 15:37 | 50.052
2019-11-24 | 15:37 | 50.053
2019-11-24 | 15:37 | 50.051
2019-11-24 | 15:37 | 50.049
2019-11-24 | 15:37 | 50.049
2019-11-24 | 15:37 | 50.051
2019-11-24 | 15:37 | 50.052
2019-11-24 | 15:37 | 50.053
2019-11-24 | 15:37 | 50.054
2019-11-24 | 15:37 | 50.054
2019-11-24 | 15:37 | 50.056
2019-11-24 | 15:37 | 50.057
2019-11-24 | 15:37 | 50.06
2019-11-24 | 15:37 | 50.061
2019-11-24 | 15:37 | 50.061
2019-11-24 | 15:37 | 50.058
2019-11-24 | 15:37 | 50.057
2019-11-24 | 15:37 | 50.055
2019-11-24 | 15:37 | 50.052
2019-11-24 | 15:37 | 50.047
2019-11-24 | 15:37 | 50.045
2019-11-24 | 15:37 | 50.041
2019-11-24 | 15:37 | 50.037
2019-11-24 | 15:37 | 50.034
2019-11-24 | 15:37 | 50.033
2019-11-24 | 15:37 | 50.032
2019-11-24 | 15:37 | 50.029
2019-11-24 | 15:37 | 50.028
2019-11-24 | 15:37 | 50.027
2019-11-24 | 15:37 | 50.026
2019-11-24 | 15:37 | 50.026
2019-11-24 | 15:37 | 50.027
2019-11-24 | 15:37 | 50.028
2019-11-24 | 15:37 | 50.027
2019-11-24 | 15:37 | 50.027
2019-11-24 | 15:37 | 50.026
2019-11-24 | 15:37 | 50.029
2019-11-24 | 15:37 | 50.026
2019-11-24 | 15:37 | 50.026
2019-11-24 | 15:37 | 50.024
2019-11-24 | 15:37 | 50.025
2019-11-24 | 15:37 | 50.025
2019-11-24 | 15:37 | 50.027
2019-11-24 | 15:37 | 50.029
2019-11-24 | 15:37 | 50.033
2019-11-24 | 15:37 | 50.035
2019-11-24 | 15:37 | 50.038
2019-11-24 | 15:37 | 50.042
2019-11-24 | 15:37 | 50.045
2019-11-24 | 15:37 | 50.044
2019-11-24 | 15:37 | 50.045
2019-11-24 | 15:37 | 50.044
2019-11-24 | 15:37 | 50.043
2019-11-24 | 15:37 | 50.042
2019-11-24 | 15:37 | 50.041
2019-11-24 | 15:37 | 50.042
2019-11-24 | 15:37 | 50.043
2019-11-24 | 15:37 | 50.041
2019-11-24 | 15:38 | 50.045
2019-11-24 | 15:38 | 50.044
2019-11-24 | 15:38 | 50.045
2019-11-24 | 15:38 | 50.045
2019-11-24 | 15:38 | 50.044
2019-11-24 | 15:38 | 50.043
2019-11-24 | 15:38 | 50.043
2019-11-24 | 15:38 | 50.042
2019-11-24 | 15:38 | 50.041
2019-11-24 | 15:38 | 50.039
2019-11-24 | 15:38 | 50.039
2019-11-24 | 15:38 | 50.038
2019-11-24 | 15:38 | 50.036
2019-11-24 | 15:38 | 50.038
2019-11-24 | 15:38 | 50.037
2019-11-24 | 15:38 | 50.038
2019-11-24 | 15:38 | 50.038
2019-11-24 | 15:38 | 50.042
2019-11-24 | 15:38 | 50.041
2019-11-24 | 15:38 | 50.043
2019-11-24 | 15:38 | 50.043
2019-11-24 | 15:38 | 50.045
2019-11-24 | 15:38 | 50.044
2019-11-24 | 15:38 | 50.043
2019-11-24 | 15:38 | 50.043
2019-11-24 | 15:38 | 50.042
2019-11-24 | 15:38 | 50.039
2019-11-24 | 15:38 | 50.037
2019-11-24 | 15:38 | 50.035
2019-11-24 | 15:38 | 50.031
2019-11-24 | 15:38 | 50.027
2019-11-24 | 15:38 | 50.025
2019-11-24 | 15:38 | 50.022
2019-11-24 | 15:38 | 50.023
2019-11-24 | 15:38 | 50.021
2019-11-24 | 15:38 | 50.021
2019-11-24 | 15:38 | 50.02
2019-11-24 | 15:38 | 50.019
2019-11-24 | 15:38 | 50.018
2019-11-24 | 15:38 | 50.017
2019-11-24 | 15:38 | 50.014
2019-11-24 | 15:38 | 50.014
2019-11-24 | 15:38 | 50.012
2019-11-24 | 15:38 | 50.012
2019-11-24 | 15:38 | 50.011
2019-11-24 | 15:38 | 50.009
2019-11-24 | 15:38 | 50.01
2019-11-24 | 15:38 | 50.01
2019-11-24 | 15:38 | 50.01
2019-11-24 | 15:38 | 50.01
2019-11-24 | 15:38 | 50.011
2019-11-24 | 15:38 | 50.008
2019-11-24 | 15:38 | 50.008
2019-11-24 | 15:38 | 50.005
2019-11-24 | 15:38 | 50.005
2019-11-24 | 15:38 | 50.002
2019-11-24 | 15:38 | 49.999
2019-11-24 | 15:38 | 49.997
2019-11-24 | 15:38 | 49.996
2019-11-24 | 15:38 | 49.995
2019-11-24 | 15:39 | 49.991
2019-11-24 | 15:39 | 49.99
2019-11-24 | 15:39 | 49.982
2019-11-24 | 15:39 | 49.975
2019-11-24 | 15:39 | 49.97
2019-11-24 | 15:39 | 49.965
2019-11-24 | 15:39 | 49.961
2019-11-24 | 15:39 | 49.958
2019-11-24 | 15:39 | 49.955
2019-11-24 | 15:39 | 49.952
2019-11-24 | 15:39 | 49.953
2019-11-24 | 15:39 | 49.954
2019-11-24 | 15:39 | 49.955
2019-11-24 | 15:39 | 49.955
2019-11-24 | 15:39 | 49.957
2019-11-24 | 15:39 | 49.957
2019-11-24 | 15:39 | 49.957
2019-11-24 | 15:39 | 49.959
2019-11-24 | 15:39 | 49.959
2019-11-24 | 15:39 | 49.959
2019-11-24 | 15:39 | 49.957
2019-11-24 | 15:39 | 49.959
2019-11-24 | 15:39 | 49.962
2019-11-24 | 15:39 | 49.962
2019-11-24 | 15:39 | 49.965
2019-11-24 | 15:39 | 49.967
2019-11-24 | 15:39 | 49.968
2019-11-24 | 15:39 | 49.97
2019-11-24 | 15:39 | 49.97
2019-11-24 | 15:39 | 49.971
2019-11-24 | 15:39 | 49.969
2019-11-24 | 15:39 | 49.969
2019-11-24 | 15:39 | 49.965
2019-11-24 | 15:39 | 49.966
2019-11-24 | 15:39 | 49.962
2019-11-24 | 15:39 | 49.961
2019-11-24 | 15:39 | 49.959
2019-11-24 | 15:39 | 49.958
2019-11-24 | 15:39 | 49.956
2019-11-24 | 15:39 | 49.953
2019-11-24 | 15:39 | 49.953
2019-11-24 | 15:39 | 49.952
2019-11-24 | 15:39 | 49.951
2019-11-24 | 15:39 | 49.949
2019-11-24 | 15:39 | 49.948
2019-11-24 | 15:39 | 49.949
2019-11-24 | 15:39 | 49.949
2019-11-24 | 15:39 | 49.952
2019-11-24 | 15:39 | 49.953
2019-11-24 | 15:39 | 49.955
2019-11-24 | 15:39 | 49.957
2019-11-24 | 15:39 | 49.957
2019-11-24 | 15:39 | 49.957
2019-11-24 | 15:39 | 49.957
2019-11-24 | 15:39 | 49.958
2019-11-24 | 15:39 | 49.959
2019-11-24 | 15:39 | 49.961
2019-11-24 | 15:39 | 49.961
2019-11-24 | 15:39 | 49.962
2019-11-24 | 15:39 | 49.961
2019-11-24 | 15:39 | 49.961
2019-11-24 | 15:40 | 49.96
2019-11-24 | 15:40 | 49.961
2019-11-24 | 15:40 | 49.964
2019-11-24 | 15:40 | 49.967
2019-11-24 | 15:40 | 49.97
2019-11-24 | 15:40 | 49.973
2019-11-24 | 15:40 | 49.975
2019-11-24 | 15:40 | 49.977
2019-11-24 | 15:40 | 49.979
2019-11-24 | 15:40 | 49.979
2019-11-24 | 15:40 | 49.979
2019-11-24 | 15:40 | 49.979
2019-11-24 | 15:40 | 49.981
2019-11-24 | 15:40 | 49.981
2019-11-24 | 15:40 | 49.984
2019-11-24 | 15:40 | 49.983
2019-11-24 | 15:40 | 49.985
2019-11-24 | 15:40 | 49.983
2019-11-24 | 15:40 | 49.985
2019-11-24 | 15:40 | 49.984
2019-11-24 | 15:40 | 49.985
2019-11-24 | 15:40 | 49.984
2019-11-24 | 15:40 | 49.984
2019-11-24 | 15:40 | 49.982
2019-11-24 | 15:40 | 49.981
2019-11-24 | 15:40 | 49.98
2019-11-24 | 15:40 | 49.983
2019-11-24 | 15:40 | 49.982
2019-11-24 | 15:40 | 49.982
2019-11-24 | 15:40 | 49.98
2019-11-24 | 15:40 | 49.978
2019-11-24 | 15:40 | 49.976
2019-11-24 | 15:40 | 49.974
2019-11-24 | 15:40 | 49.974
2019-11-24 | 15:40 | 49.972
2019-11-24 | 15:40 | 49.97
2019-11-24 | 15:40 | 49.97
2019-11-24 | 15:40 | 49.967
2019-11-24 | 15:40 | 49.966
2019-11-24 | 15:40 | 49.964
2019-11-24 | 15:40 | 49.968
2019-11-24 | 15:40 | 49.97
2019-11-24 | 15:40 | 49.973
2019-11-24 | 15:40 | 49.975
2019-11-24 | 15:40 | 49.976
2019-11-24 | 15:40 | 49.981
2019-11-24 | 15:40 | 49.983
2019-11-24 | 15:40 | 49.983
2019-11-24 | 15:40 | 49.983
2019-11-24 | 15:40 | 49.982
2019-11-24 | 15:40 | 49.978
2019-11-24 | 15:40 | 49.98
2019-11-24 | 15:40 | 49.979
2019-11-24 | 15:40 | 49.979
2019-11-24 | 15:40 | 49.978
2019-11-24 | 15:40 | 49.978
2019-11-24 | 15:40 | 49.978
2019-11-24 | 15:40 | 49.976
2019-11-24 | 15:40 | 49.975
2019-11-24 | 15:41 | 49.977
2019-11-24 | 15:41 | 49.979
2019-11-24 | 15:41 | 49.979
2019-11-24 | 15:41 | 49.984
2019-11-24 | 15:41 | 49.987
2019-11-24 | 15:41 | 49.992
2019-11-24 | 15:41 | 49.995
2019-11-24 | 15:41 | 49.998
2019-11-24 | 15:41 | 50
2019-11-24 | 15:41 | 50.001
2019-11-24 | 15:41 | 50
2019-11-24 | 15:41 | 49.998
2019-11-24 | 15:41 | 49.997
2019-11-24 | 15:41 | 49.995
2019-11-24 | 15:41 | 49.994
2019-11-24 | 15:41 | 49.998
2019-11-24 | 15:41 | 49.995
2019-11-24 | 15:41 | 49.997
2019-11-24 | 15:41 | 49.996
2019-11-24 | 15:41 | 49.995
2019-11-24 | 15:41 | 49.992
2019-11-24 | 15:41 | 49.991
2019-11-24 | 15:41 | 49.991
2019-11-24 | 15:41 | 49.988
2019-11-24 | 15:41 | 49.987
2019-11-24 | 15:41 | 49.984
2019-11-24 | 15:41 | 49.981
2019-11-24 | 15:41 | 49.98
2019-11-24 | 15:41 | 49.976
2019-11-24 | 15:41 | 49.977
2019-11-24 | 15:41 | 49.976
2019-11-24 | 15:41 | 49.976
2019-11-24 | 15:41 | 49.976
2019-11-24 | 15:41 | 49.978
2019-11-24 | 15:41 | 49.978
2019-11-24 | 15:41 | 49.982
2019-11-24 | 15:41 | 49.982
2019-11-24 | 15:41 | 49.985
2019-11-24 | 15:41 | 49.983
2019-11-24 | 15:41 | 49.983
2019-11-24 | 15:41 | 49.982
2019-11-24 | 15:41 | 49.981
2019-11-24 | 15:41 | 49.979
2019-11-24 | 15:41 | 49.976
2019-11-24 | 15:41 | 49.973
2019-11-24 | 15:41 | 49.972
2019-11-24 | 15:41 | 49.971
2019-11-24 | 15:41 | 49.971
2019-11-24 | 15:41 | 49.97
2019-11-24 | 15:41 | 49.969
2019-11-24 | 15:41 | 49.965
2019-11-24 | 15:41 | 49.965
2019-11-24 | 15:41 | 49.963
2019-11-24 | 15:41 | 49.959
2019-11-24 | 15:41 | 49.955
2019-11-24 | 15:41 | 49.955
2019-11-24 | 15:41 | 49.952
2019-11-24 | 15:41 | 49.95
2019-11-24 | 15:41 | 49.946
2019-11-24 | 15:41 | 49.947
2019-11-24 | 15:41 | 49.948
2019-11-24 | 15:42 | 49.949
2019-11-24 | 15:42 | 49.948
2019-11-24 | 15:42 | 49.95
2019-11-24 | 15:42 | 49.95
2019-11-24 | 15:42 | 49.949
2019-11-24 | 15:42 | 49.95
2019-11-24 | 15:42 | 49.949
2019-11-24 | 15:42 | 49.949
2019-11-24 | 15:42 | 49.95
2019-11-24 | 15:42 | 49.95
2019-11-24 | 15:42 | 49.949
2019-11-24 | 15:42 | 49.948
2019-11-24 | 15:42 | 49.947
2019-11-24 | 15:42 | 49.949
2019-11-24 | 15:42 | 49.947
2019-11-24 | 15:42 | 49.95
2019-11-24 | 15:42 | 49.949
2019-11-24 | 15:42 | 49.949
2019-11-24 | 15:42 | 49.951
2019-11-24 | 15:42 | 49.948
2019-11-24 | 15:42 | 49.949
2019-11-24 | 15:42 | 49.949
2019-11-24 | 15:42 | 49.949
2019-11-24 | 15:42 | 49.951
2019-11-24 | 15:42 | 49.954
2019-11-24 | 15:42 | 49.958
2019-11-24 | 15:42 | 49.96
2019-11-24 | 15:42 | 49.964
2019-11-24 | 15:42 | 49.966
2019-11-24 | 15:42 | 49.968
2019-11-24 | 15:42 | 49.971
2019-11-24 | 15:42 | 49.973
2019-11-24 | 15:42 | 49.975
2019-11-24 | 15:42 | 49.976
2019-11-24 | 15:42 | 49.976
2019-11-24 | 15:42 | 49.974
2019-11-24 | 15:42 | 49.975
2019-11-24 | 15:42 | 49.973
2019-11-24 | 15:42 | 49.975
2019-11-24 | 15:42 | 49.976
2019-11-24 | 15:42 | 49.978
2019-11-24 | 15:42 | 49.979
2019-11-24 | 15:42 | 49.981
2019-11-24 | 15:42 | 49.98
2019-11-24 | 15:42 | 49.983
2019-11-24 | 15:42 | 49.98
2019-11-24 | 15:42 | 49.981
2019-11-24 | 15:42 | 49.981
2019-11-24 | 15:42 | 49.98
2019-11-24 | 15:42 | 49.98
2019-11-24 | 15:42 | 49.978
2019-11-24 | 15:42 | 49.976
2019-11-24 | 15:42 | 49.974
2019-11-24 | 15:42 | 49.974
2019-11-24 | 15:42 | 49.976
2019-11-24 | 15:42 | 49.976
2019-11-24 | 15:42 | 49.977
2019-11-24 | 15:42 | 49.977
2019-11-24 | 15:42 | 49.977
2019-11-24 | 15:43 | 49.977
2019-11-24 | 15:43 | 49.975
2019-11-24 | 15:43 | 49.976
2019-11-24 | 15:43 | 49.973
2019-11-24 | 15:43 | 49.975
2019-11-24 | 15:43 | 49.969
2019-11-24 | 15:43 | 49.969
2019-11-24 | 15:43 | 49.967
2019-11-24 | 15:43 | 49.968
2019-11-24 | 15:43 | 49.971
2019-11-24 | 15:43 | 49.974
2019-11-24 | 15:43 | 49.978
2019-11-24 | 15:43 | 49.978
2019-11-24 | 15:43 | 49.983
2019-11-24 | 15:43 | 49.985
2019-11-24 | 15:43 | 49.988
2019-11-24 | 15:43 | 49.987
2019-11-24 | 15:43 | 49.987
2019-11-24 | 15:43 | 49.984
2019-11-24 | 15:43 | 49.984
2019-11-24 | 15:43 | 49.982
2019-11-24 | 15:43 | 49.98
2019-11-24 | 15:43 | 49.979
2019-11-24 | 15:43 | 49.98
2019-11-24 | 15:43 | 49.977
2019-11-24 | 15:43 | 49.976
2019-11-24 | 15:43 | 49.978
2019-11-24 | 15:43 | 49.977
2019-11-24 | 15:43 | 49.976
2019-11-24 | 15:43 | 49.974
2019-11-24 | 15:43 | 49.974
2019-11-24 | 15:43 | 49.973
2019-11-24 | 15:43 | 49.975
2019-11-24 | 15:43 | 49.974
2019-11-24 | 15:43 | 49.978
2019-11-24 | 15:43 | 49.979
2019-11-24 | 15:43 | 49.981
2019-11-24 | 15:43 | 49.979
2019-11-24 | 15:43 | 49.982
2019-11-24 | 15:43 | 49.982
2019-11-24 | 15:43 | 49.982
2019-11-24 | 15:43 | 49.983
2019-11-24 | 15:43 | 49.98
2019-11-24 | 15:43 | 49.981
2019-11-24 | 15:43 | 49.977
2019-11-24 | 15:43 | 49.977
2019-11-24 | 15:43 | 49.977
2019-11-24 | 15:43 | 49.976
2019-11-24 | 15:43 | 49.979
2019-11-24 | 15:43 | 49.978
2019-11-24 | 15:43 | 49.979
2019-11-24 | 15:43 | 49.98
2019-11-24 | 15:43 | 49.979
2019-11-24 | 15:43 | 49.981
2019-11-24 | 15:43 | 49.981
2019-11-24 | 15:43 | 49.984
2019-11-24 | 15:43 | 49.984
2019-11-24 | 15:43 | 49.984
2019-11-24 | 15:43 | 49.984
2019-11-24 | 15:43 | 49.984
2019-11-24 | 15:43 | 49.983
2019-11-24 | 15:44 | 49.983
2019-11-24 | 15:44 | 49.984
2019-11-24 | 15:44 | 49.982
2019-11-24 | 15:44 | 49.983
2019-11-24 | 15:44 | 49.981
2019-11-24 | 15:44 | 49.98
2019-11-24 | 15:44 | 49.975
2019-11-24 | 15:44 | 49.973
2019-11-24 | 15:44 | 49.967
2019-11-24 | 15:44 | 49.967
2019-11-24 | 15:44 | 49.965
2019-11-24 | 15:44 | 49.964
2019-11-24 | 15:44 | 49.963
2019-11-24 | 15:44 | 49.964
2019-11-24 | 15:44 | 49.962
2019-11-24 | 15:44 | 49.962
2019-11-24 | 15:44 | 49.964
2019-11-24 | 15:44 | 49.968
2019-11-24 | 15:44 | 49.967
2019-11-24 | 15:44 | 49.969
2019-11-24 | 15:44 | 49.968
2019-11-24 | 15:44 | 49.965
2019-11-24 | 15:44 | 49.965
2019-11-24 | 15:44 | 49.963
2019-11-24 | 15:44 | 49.961
2019-11-24 | 15:44 | 49.962
2019-11-24 | 15:44 | 49.96
2019-11-24 | 15:44 | 49.961
2019-11-24 | 15:44 | 49.957
2019-11-24 | 15:44 | 49.958
2019-11-24 | 15:44 | 49.958
2019-11-24 | 15:44 | 49.958
2019-11-24 | 15:44 | 49.961
2019-11-24 | 15:44 | 49.96
2019-11-24 | 15:44 | 49.963
2019-11-24 | 15:44 | 49.962
2019-11-24 | 15:44 | 49.962
2019-11-24 | 15:44 | 49.963
2019-11-24 | 15:44 | 49.961
2019-11-24 | 15:44 | 49.962
2019-11-24 | 15:44 | 49.963
2019-11-24 | 15:44 | 49.964
2019-11-24 | 15:44 | 49.965
2019-11-24 | 15:44 | 49.965
2019-11-24 | 15:44 | 49.966
2019-11-24 | 15:44 | 49.967
2019-11-24 | 15:44 | 49.967
2019-11-24 | 15:44 | 49.969
2019-11-24 | 15:44 | 49.97
2019-11-24 | 15:44 | 49.97
2019-11-24 | 15:44 | 49.971
2019-11-24 | 15:44 | 49.97
2019-11-24 | 15:44 | 49.97
2019-11-24 | 15:44 | 49.969
2019-11-24 | 15:44 | 49.967
2019-11-24 | 15:44 | 49.966
2019-11-24 | 15:44 | 49.964
2019-11-24 | 15:44 | 49.964
2019-11-24 | 15:44 | 49.961
2019-11-24 | 15:45 | 49.962
2019-11-24 | 15:45 | 49.962
2019-11-24 | 15:45 | 49.964
2019-11-24 | 15:45 | 49.967
2019-11-24 | 15:45 | 49.967
2019-11-24 | 15:45 | 49.969
2019-11-24 | 15:45 | 49.971
2019-11-24 | 15:45 | 49.97
2019-11-24 | 15:45 | 49.97
2019-11-24 | 15:45 | 49.97
2019-11-24 | 15:45 | 49.967
2019-11-24 | 15:45 | 49.968
2019-11-24 | 15:45 | 49.968
2019-11-24 | 15:45 | 49.966
2019-11-24 | 15:45 | 49.968
2019-11-24 | 15:45 | 49.968
2019-11-24 | 15:45 | 49.966
2019-11-24 | 15:45 | 49.968
2019-11-24 | 15:45 | 49.968
2019-11-24 | 15:45 | 49.971
2019-11-24 | 15:45 | 49.97
2019-11-24 | 15:45 | 49.97
2019-11-24 | 15:45 | 49.971
2019-11-24 | 15:45 | 49.97
2019-11-24 | 15:45 | 49.972
2019-11-24 | 15:45 | 49.973
2019-11-24 | 15:45 | 49.976
2019-11-24 | 15:45 | 49.977
2019-11-24 | 15:45 | 49.978
2019-11-24 | 15:45 | 49.977
2019-11-24 | 15:45 | 49.976
2019-11-24 | 15:45 | 49.975
2019-11-24 | 15:45 | 49.973
2019-11-24 | 15:45 | 49.97
2019-11-24 | 15:45 | 49.97
2019-11-24 | 15:45 | 49.967
2019-11-24 | 15:45 | 49.97
2019-11-24 | 15:45 | 49.969
2019-11-24 | 15:45 | 49.971
2019-11-24 | 15:45 | 49.972
2019-11-24 | 15:45 | 49.975
2019-11-24 | 15:45 | 49.976
2019-11-24 | 15:45 | 49.978
2019-11-24 | 15:45 | 49.976
2019-11-24 | 15:45 | 49.974
2019-11-24 | 15:45 | 49.974
2019-11-24 | 15:45 | 49.973
2019-11-24 | 15:45 | 49.97
2019-11-24 | 15:45 | 49.965
2019-11-24 | 15:45 | 49.962
2019-11-24 | 15:45 | 49.961
2019-11-24 | 15:45 | 49.959
2019-11-24 | 15:45 | 49.96
2019-11-24 | 15:45 | 49.956
2019-11-24 | 15:45 | 49.955
2019-11-24 | 15:45 | 49.953
2019-11-24 | 15:45 | 49.95
2019-11-24 | 15:45 | 49.949
2019-11-24 | 15:45 | 49.948
2019-11-24 | 15:45 | 49.945
2019-11-24 | 15:45 | 49.947
2019-11-24 | 15:46 | 49.943
2019-11-24 | 15:46 | 49.945
2019-11-24 | 15:46 | 49.943
2019-11-24 | 15:46 | 49.943
2019-11-24 | 15:46 | 49.943
2019-11-24 | 15:46 | 49.942
2019-11-24 | 15:46 | 49.943
2019-11-24 | 15:46 | 49.94
2019-11-24 | 15:46 | 49.943
2019-11-24 | 15:46 | 49.941
2019-11-24 | 15:46 | 49.943
2019-11-24 | 15:46 | 49.941
2019-11-24 | 15:46 | 49.943
2019-11-24 | 15:46 | 49.943
2019-11-24 | 15:46 | 49.944
2019-11-24 | 15:46 | 49.946
2019-11-24 | 15:46 | 49.948
2019-11-24 | 15:46 | 49.951
2019-11-24 | 15:46 | 49.951
2019-11-24 | 15:46 | 49.953
2019-11-24 | 15:46 | 49.953
2019-11-24 | 15:46 | 49.956
2019-11-24 | 15:46 | 49.952
2019-11-24 | 15:46 | 49.955
2019-11-24 | 15:46 | 49.954
2019-11-24 | 15:46 | 49.955
2019-11-24 | 15:46 | 49.956
2019-11-24 | 15:46 | 49.958
2019-11-24 | 15:46 | 49.956
2019-11-24 | 15:46 | 49.957
2019-11-24 | 15:46 | 49.955
2019-11-24 | 15:46 | 49.953
2019-11-24 | 15:46 | 49.953
2019-11-24 | 15:46 | 49.951
2019-11-24 | 15:46 | 49.949
2019-11-24 | 15:46 | 49.948
2019-11-24 | 15:46 | 49.945
2019-11-24 | 15:46 | 49.944
2019-11-24 | 15:46 | 49.944
2019-11-24 | 15:46 | 49.942
2019-11-24 | 15:46 | 49.942
2019-11-24 | 15:46 | 49.944
2019-11-24 | 15:46 | 49.943
2019-11-24 | 15:46 | 49.942
2019-11-24 | 15:46 | 49.942
2019-11-24 | 15:46 | 49.94
2019-11-24 | 15:46 | 49.94
2019-11-24 | 15:46 | 49.938
2019-11-24 | 15:46 | 49.938
2019-11-24 | 15:46 | 49.937
2019-11-24 | 15:46 | 49.935
2019-11-24 | 15:46 | 49.936
2019-11-24 | 15:46 | 49.936
2019-11-24 | 15:46 | 49.935
2019-11-24 | 15:46 | 49.935
2019-11-24 | 15:46 | 49.937
2019-11-24 | 15:46 | 49.936
2019-11-24 | 15:46 | 49.937
2019-11-24 | 15:46 | 49.936
2019-11-24 | 15:47 | 49.938
2019-11-24 | 15:47 | 49.938
2019-11-24 | 15:47 | 49.938
2019-11-24 | 15:47 | 49.941
2019-11-24 | 15:47 | 49.942
2019-11-24 | 15:47 | 49.943
2019-11-24 | 15:47 | 49.943
2019-11-24 | 15:47 | 49.943
2019-11-24 | 15:47 | 49.944
2019-11-24 | 15:47 | 49.946
2019-11-24 | 15:47 | 49.945
2019-11-24 | 15:47 | 49.947
2019-11-24 | 15:47 | 49.946
2019-11-24 | 15:47 | 49.946
2019-11-24 | 15:47 | 49.945
2019-11-24 | 15:47 | 49.944
2019-11-24 | 15:47 | 49.942
2019-11-24 | 15:47 | 49.942
2019-11-24 | 15:47 | 49.941
2019-11-24 | 15:47 | 49.941
2019-11-24 | 15:47 | 49.943
2019-11-24 | 15:47 | 49.941
2019-11-24 | 15:47 | 49.942
2019-11-24 | 15:47 | 49.941
2019-11-24 | 15:47 | 49.938
2019-11-24 | 15:47 | 49.939
2019-11-24 | 15:47 | 49.934
2019-11-24 | 15:47 | 49.933
2019-11-24 | 15:47 | 49.934
2019-11-24 | 15:47 | 49.934
2019-11-24 | 15:47 | 49.936
2019-11-24 | 15:47 | 49.939
2019-11-24 | 15:47 | 49.94
2019-11-24 | 15:47 | 49.94
2019-11-24 | 15:47 | 49.944
2019-11-24 | 15:47 | 49.945
2019-11-24 | 15:47 | 49.949
2019-11-24 | 15:47 | 49.95
2019-11-24 | 15:47 | 49.951
2019-11-24 | 15:47 | 49.951
2019-11-24 | 15:47 | 49.95
2019-11-24 | 15:47 | 49.949
2019-11-24 | 15:47 | 49.947
2019-11-24 | 15:47 | 49.946
2019-11-24 | 15:47 | 49.948
2019-11-24 | 15:47 | 49.948
2019-11-24 | 15:47 | 49.949
2019-11-24 | 15:47 | 49.95
2019-11-24 | 15:47 | 49.953
2019-11-24 | 15:47 | 49.955
2019-11-24 | 15:47 | 49.956
2019-11-24 | 15:47 | 49.957
2019-11-24 | 15:47 | 49.958
2019-11-24 | 15:47 | 49.956
2019-11-24 | 15:47 | 49.955
2019-11-24 | 15:47 | 49.952
2019-11-24 | 15:47 | 49.948
2019-11-24 | 15:47 | 49.947
2019-11-24 | 15:47 | 49.948
2019-11-24 | 15:47 | 49.946
2019-11-24 | 15:47 | 49.95
2019-11-24 | 15:48 | 49.952
2019-11-24 | 15:48 | 49.954
2019-11-24 | 15:48 | 49.958
2019-11-24 | 15:48 | 49.959
2019-11-24 | 15:48 | 49.962
2019-11-24 | 15:48 | 49.965
2019-11-24 | 15:48 | 49.966
2019-11-24 | 15:48 | 49.971
2019-11-24 | 15:48 | 49.974
2019-11-24 | 15:48 | 49.975
2019-11-24 | 15:48 | 49.975
2019-11-24 | 15:48 | 49.975
2019-11-24 | 15:48 | 49.971
2019-11-24 | 15:48 | 49.97
2019-11-24 | 15:48 | 49.968
2019-11-24 | 15:48 | 49.967
2019-11-24 | 15:48 | 49.962
2019-11-24 | 15:48 | 49.961
2019-11-24 | 15:48 | 49.959
2019-11-24 | 15:48 | 49.957
2019-11-24 | 15:48 | 49.956
2019-11-24 | 15:48 | 49.953
2019-11-24 | 15:48 | 49.952
2019-11-24 | 15:48 | 49.952
2019-11-24 | 15:48 | 49.948
2019-11-24 | 15:48 | 49.947
2019-11-24 | 15:48 | 49.944
2019-11-24 | 15:48 | 49.943
2019-11-24 | 15:48 | 49.94
2019-11-24 | 15:48 | 49.937
2019-11-24 | 15:48 | 49.934
2019-11-24 | 15:48 | 49.932
2019-11-24 | 15:48 | 49.93
2019-11-24 | 15:48 | 49.928
2019-11-24 | 15:48 | 49.928
2019-11-24 | 15:48 | 49.927
2019-11-24 | 15:48 | 49.927
2019-11-24 | 15:48 | 49.929
2019-11-24 | 15:48 | 49.929
2019-11-24 | 15:48 | 49.932
2019-11-24 | 15:48 | 49.931
2019-11-24 | 15:48 | 49.933
2019-11-24 | 15:48 | 49.934
2019-11-24 | 15:48 | 49.934
2019-11-24 | 15:48 | 49.934
2019-11-24 | 15:48 | 49.935
2019-11-24 | 15:48 | 49.933
2019-11-24 | 15:48 | 49.931
2019-11-24 | 15:48 | 49.93
2019-11-24 | 15:48 | 49.928
2019-11-24 | 15:48 | 49.927
2019-11-24 | 15:48 | 49.923
2019-11-24 | 15:48 | 49.921
2019-11-24 | 15:48 | 49.919
2019-11-24 | 15:48 | 49.919
2019-11-24 | 15:48 | 49.918
2019-11-24 | 15:48 | 49.916
2019-11-24 | 15:48 | 49.917
2019-11-24 | 15:48 | 49.919
2019-11-24 | 15:49 | 49.92
2019-11-24 | 15:49 | 49.922
2019-11-24 | 15:49 | 49.921
2019-11-24 | 15:49 | 49.924
2019-11-24 | 15:49 | 49.922
2019-11-24 | 15:49 | 49.92
2019-11-24 | 15:49 | 49.919
2019-11-24 | 15:49 | 49.916
2019-11-24 | 15:49 | 49.914
2019-11-24 | 15:49 | 49.911
2019-11-24 | 15:49 | 49.909
2019-11-24 | 15:49 | 49.907
2019-11-24 | 15:49 | 49.904
2019-11-24 | 15:49 | 49.904
2019-11-24 | 15:49 | 49.903
2019-11-24 | 15:49 | 49.903
2019-11-24 | 15:49 | 49.904
2019-11-24 | 15:49 | 49.902
2019-11-24 | 15:49 | 49.904
2019-11-24 | 15:49 | 49.905
2019-11-24 | 15:49 | 49.904
2019-11-24 | 15:49 | 49.906
2019-11-24 | 15:49 | 49.905
2019-11-24 | 15:49 | 49.904
2019-11-24 | 15:49 | 49.905
2019-11-24 | 15:49 | 49.905
2019-11-24 | 15:49 | 49.905
2019-11-24 | 15:49 | 49.908
2019-11-24 | 15:49 | 49.908
2019-11-24 | 15:49 | 49.908
2019-11-24 | 15:49 | 49.91
2019-11-24 | 15:49 | 49.909
2019-11-24 | 15:49 | 49.91
2019-11-24 | 15:49 | 49.911
2019-11-24 | 15:49 | 49.909
2019-11-24 | 15:49 | 49.909
2019-11-24 | 15:49 | 49.908
2019-11-24 | 15:49 | 49.906
2019-11-24 | 15:49 | 49.906
2019-11-24 | 15:49 | 49.911
2019-11-24 | 15:49 | 49.913
2019-11-24 | 15:49 | 49.916
2019-11-24 | 15:49 | 49.918
2019-11-24 | 15:49 | 49.921
2019-11-24 | 15:49 | 49.922
2019-11-24 | 15:49 | 49.925
2019-11-24 | 15:49 | 49.927
2019-11-24 | 15:49 | 49.925
2019-11-24 | 15:49 | 49.923
2019-11-24 | 15:49 | 49.92
2019-11-24 | 15:49 | 49.917
2019-11-24 | 15:49 | 49.914
2019-11-24 | 15:49 | 49.91
2019-11-24 | 15:49 | 49.909
2019-11-24 | 15:49 | 49.908
2019-11-24 | 15:49 | 49.907
2019-11-24 | 15:49 | 49.91
2019-11-24 | 15:49 | 49.91
2019-11-24 | 15:49 | 49.91
2019-11-24 | 15:49 | 49.911
2019-11-24 | 15:49 | 49.912
2019-11-24 | 15:50 | 49.912
2019-11-24 | 15:50 | 49.911
2019-11-24 | 15:50 | 49.91
2019-11-24 | 15:50 | 49.91
2019-11-24 | 15:50 | 49.906
2019-11-24 | 15:50 | 49.904
2019-11-24 | 15:50 | 49.903
2019-11-24 | 15:50 | 49.904
2019-11-24 | 15:50 | 49.904
2019-11-24 | 15:50 | 49.903
2019-11-24 | 15:50 | 49.906
2019-11-24 | 15:50 | 49.906
2019-11-24 | 15:50 | 49.907
2019-11-24 | 15:50 | 49.908
2019-11-24 | 15:50 | 49.909
2019-11-24 | 15:50 | 49.909
2019-11-24 | 15:50 | 49.91
2019-11-24 | 15:50 | 49.911
2019-11-24 | 15:50 | 49.911
2019-11-24 | 15:50 | 49.909
2019-11-24 | 15:50 | 49.908
2019-11-24 | 15:50 | 49.904
2019-11-24 | 15:50 | 49.903
2019-11-24 | 15:50 | 49.9
2019-11-24 | 15:50 | 49.898
2019-11-24 | 15:50 | 49.897
2019-11-24 | 15:50 | 49.898
2019-11-24 | 15:50 | 49.9
2019-11-24 | 15:50 | 49.902
2019-11-24 | 15:50 | 49.904
2019-11-24 | 15:50 | 49.905
2019-11-24 | 15:50 | 49.907
2019-11-24 | 15:50 | 49.906
2019-11-24 | 15:50 | 49.906
2019-11-24 | 15:50 | 49.908
2019-11-24 | 15:50 | 49.908
2019-11-24 | 15:50 | 49.907
2019-11-24 | 15:50 | 49.908
2019-11-24 | 15:50 | 49.908
2019-11-24 | 15:50 | 49.91
2019-11-24 | 15:50 | 49.91
2019-11-24 | 15:50 | 49.91
2019-11-24 | 15:50 | 49.909
2019-11-24 | 15:50 | 49.909
2019-11-24 | 15:50 | 49.909
2019-11-24 | 15:50 | 49.91
2019-11-24 | 15:50 | 49.91
2019-11-24 | 15:50 | 49.911
2019-11-24 | 15:50 | 49.909
2019-11-24 | 15:50 | 49.909
2019-11-24 | 15:50 | 49.91
2019-11-24 | 15:50 | 49.909
2019-11-24 | 15:50 | 49.907
2019-11-24 | 15:50 | 49.907
2019-11-24 | 15:50 | 49.904
2019-11-24 | 15:50 | 49.902
2019-11-24 | 15:50 | 49.901
2019-11-24 | 15:50 | 49.901
2019-11-24 | 15:50 | 49.9
2019-11-24 | 15:51 | 49.901
2019-11-24 | 15:51 | 49.902
2019-11-24 | 15:51 | 49.901
2019-11-24 | 15:51 | 49.901
2019-11-24 | 15:51 | 49.901
2019-11-24 | 15:51 | 49.901
2019-11-24 | 15:51 | 49.9
2019-11-24 | 15:51 | 49.9
2019-11-24 | 15:51 | 49.901
2019-11-24 | 15:51 | 49.901
2019-11-24 | 15:51 | 49.9
2019-11-24 | 15:51 | 49.899
2019-11-24 | 15:51 | 49.899
2019-11-24 | 15:51 | 49.899
2019-11-24 | 15:51 | 49.898
2019-11-24 | 15:51 | 49.901
2019-11-24 | 15:51 | 49.903
2019-11-24 | 15:51 | 49.904
2019-11-24 | 15:51 | 49.906
2019-11-24 | 15:51 | 49.906
2019-11-24 | 15:51 | 49.908
2019-11-24 | 15:51 | 49.909
2019-11-24 | 15:51 | 49.911
2019-11-24 | 15:51 | 49.911
2019-11-24 | 15:51 | 49.913
2019-11-24 | 15:51 | 49.915
2019-11-24 | 15:51 | 49.916
2019-11-24 | 15:51 | 49.917
2019-11-24 | 15:51 | 49.917
2019-11-24 | 15:51 | 49.918
2019-11-24 | 15:51 | 49.918
2019-11-24 | 15:51 | 49.917
2019-11-24 | 15:51 | 49.916
2019-11-24 | 15:51 | 49.917
2019-11-24 | 15:51 | 49.918
2019-11-24 | 15:51 | 49.918
2019-11-24 | 15:51 | 49.92
2019-11-24 | 15:51 | 49.919
2019-11-24 | 15:51 | 49.918
2019-11-24 | 15:51 | 49.919
2019-11-24 | 15:51 | 49.916
2019-11-24 | 15:51 | 49.913
2019-11-24 | 15:51 | 49.911
2019-11-24 | 15:51 | 49.91
2019-11-24 | 15:51 | 49.91
2019-11-24 | 15:51 | 49.912
2019-11-24 | 15:51 | 49.912
2019-11-24 | 15:51 | 49.913
2019-11-24 | 15:51 | 49.912
2019-11-24 | 15:51 | 49.912
2019-11-24 | 15:51 | 49.912
2019-11-24 | 15:51 | 49.911
2019-11-24 | 15:51 | 49.911
2019-11-24 | 15:51 | 49.911
2019-11-24 | 15:51 | 49.91
2019-11-24 | 15:51 | 49.907
2019-11-24 | 15:51 | 49.905
2019-11-24 | 15:51 | 49.903
2019-11-24 | 15:51 | 49.901
2019-11-24 | 15:51 | 49.901
2019-11-24 | 15:51 | 49.901
2019-11-24 | 15:52 | 49.904
2019-11-24 | 15:52 | 49.904
2019-11-24 | 15:52 | 49.903
2019-11-24 | 15:52 | 49.904
2019-11-24 | 15:52 | 49.903
2019-11-24 | 15:52 | 49.902
2019-11-24 | 15:52 | 49.9
2019-11-24 | 15:52 | 49.898
2019-11-24 | 15:52 | 49.897
2019-11-24 | 15:52 | 49.895
2019-11-24 | 15:52 | 49.894
2019-11-24 | 15:52 | 49.893
2019-11-24 | 15:52 | 49.892
2019-11-24 | 15:52 | 49.889
2019-11-24 | 15:52 | 49.887
2019-11-24 | 15:52 | 49.885
2019-11-24 | 15:52 | 49.885
2019-11-24 | 15:52 | 49.884
2019-11-24 | 15:52 | 49.883
2019-11-24 | 15:52 | 49.882
2019-11-24 | 15:52 | 49.881
2019-11-24 | 15:52 | 49.88
2019-11-24 | 15:52 | 49.879
2019-11-24 | 15:52 | 49.878
2019-11-24 | 15:52 | 49.877
2019-11-24 | 15:52 | 49.876
2019-11-24 | 15:52 | 49.876
2019-11-24 | 15:52 | 49.876
2019-11-24 | 15:52 | 49.876
2019-11-24 | 15:52 | 49.877
2019-11-24 | 15:52 | 49.876
2019-11-24 | 15:52 | 49.878
2019-11-24 | 15:52 | 49.881
2019-11-24 | 15:52 | 49.883
2019-11-24 | 15:52 | 49.886
2019-11-24 | 15:52 | 49.889
2019-11-24 | 15:52 | 49.89
2019-11-24 | 15:52 | 49.892
2019-11-24 | 15:52 | 49.893
2019-11-24 | 15:52 | 49.897
2019-11-24 | 15:52 | 49.899
2019-11-24 | 15:52 | 49.899
2019-11-24 | 15:52 | 49.901
2019-11-24 | 15:52 | 49.903
2019-11-24 | 15:52 | 49.904
2019-11-24 | 15:52 | 49.906
2019-11-24 | 15:52 | 49.909
2019-11-24 | 15:52 | 49.908
2019-11-24 | 15:52 | 49.907
2019-11-24 | 15:52 | 49.911
2019-11-24 | 15:52 | 49.913
2019-11-24 | 15:52 | 49.915
2019-11-24 | 15:52 | 49.916
2019-11-24 | 15:52 | 49.918
2019-11-24 | 15:52 | 49.92
2019-11-24 | 15:52 | 49.92
2019-11-24 | 15:52 | 49.919
2019-11-24 | 15:52 | 49.92
2019-11-24 | 15:52 | 49.918
2019-11-24 | 15:52 | 49.915
2019-11-24 | 15:53 | 49.913
2019-11-24 | 15:53 | 49.91
2019-11-24 | 15:53 | 49.91
2019-11-24 | 15:53 | 49.908
2019-11-24 | 15:53 | 49.907
2019-11-24 | 15:53 | 49.906
2019-11-24 | 15:53 | 49.905
2019-11-24 | 15:53 | 49.904
2019-11-24 | 15:53 | 49.902
2019-11-24 | 15:53 | 49.901
2019-11-24 | 15:53 | 49.899
2019-11-24 | 15:53 | 49.897
2019-11-24 | 15:53 | 49.895
2019-11-24 | 15:53 | 49.893
2019-11-24 | 15:53 | 49.891
2019-11-24 | 15:53 | 49.89
2019-11-24 | 15:53 | 49.889
2019-11-24 | 15:53 | 49.888
2019-11-24 | 15:53 | 49.889
2019-11-24 | 15:53 | 49.89
2019-11-24 | 15:53 | 49.893
2019-11-24 | 15:53 | 49.893
2019-11-24 | 15:53 | 49.894
2019-11-24 | 15:53 | 49.897
2019-11-24 | 15:53 | 49.896
2019-11-24 | 15:53 | 49.897
2019-11-24 | 15:53 | 49.896
2019-11-24 | 15:53 | 49.895
2019-11-24 | 15:53 | 49.896
2019-11-24 | 15:53 | 49.892
2019-11-24 | 15:53 | 49.889
2019-11-24 | 15:53 | 49.888
2019-11-24 | 15:53 | 49.884
2019-11-24 | 15:53 | 49.878
2019-11-24 | 15:53 | 49.876
2019-11-24 | 15:53 | 49.873
2019-11-24 | 15:53 | 49.872
2019-11-24 | 15:53 | 49.871
2019-11-24 | 15:53 | 49.871
2019-11-24 | 15:53 | 49.871
2019-11-24 | 15:53 | 49.87
2019-11-24 | 15:53 | 49.87
2019-11-24 | 15:53 | 49.871
2019-11-24 | 15:53 | 49.871
2019-11-24 | 15:53 | 49.869
2019-11-24 | 15:53 | 49.868
2019-11-24 | 15:53 | 49.867
2019-11-24 | 15:53 | 49.868
2019-11-24 | 15:53 | 49.869
2019-11-24 | 15:53 | 49.87
2019-11-24 | 15:53 | 49.871
2019-11-24 | 15:53 | 49.874
2019-11-24 | 15:53 | 49.876
2019-11-24 | 15:53 | 49.877
2019-11-24 | 15:53 | 49.879
2019-11-24 | 15:53 | 49.877
2019-11-24 | 15:53 | 49.875
2019-11-24 | 15:53 | 49.873
2019-11-24 | 15:53 | 49.87
2019-11-24 | 15:54 | 49.866
2019-11-24 | 15:54 | 49.866
2019-11-24 | 15:54 | 49.867
2019-11-24 | 15:54 | 49.87
2019-11-24 | 15:54 | 49.873
2019-11-24 | 15:54 | 49.875
2019-11-24 | 15:54 | 49.878
2019-11-24 | 15:54 | 49.881
2019-11-24 | 15:54 | 49.882
2019-11-24 | 15:54 | 49.883
2019-11-24 | 15:54 | 49.882
2019-11-24 | 15:54 | 49.879
2019-11-24 | 15:54 | 49.875
2019-11-24 | 15:54 | 49.868
2019-11-24 | 15:54 | 49.864
2019-11-24 | 15:54 | 49.858
2019-11-24 | 15:54 | 49.856
2019-11-24 | 15:54 | 49.855
2019-11-24 | 15:54 | 49.853
2019-11-24 | 15:54 | 49.855
2019-11-24 | 15:54 | 49.856
2019-11-24 | 15:54 | 49.855
2019-11-24 | 15:54 | 49.857
2019-11-24 | 15:54 | 49.858
2019-11-24 | 15:54 | 49.86
2019-11-24 | 15:54 | 49.863
2019-11-24 | 15:54 | 49.864
2019-11-24 | 15:54 | 49.867
2019-11-24 | 15:54 | 49.869
2019-11-24 | 15:54 | 49.87
2019-11-24 | 15:54 | 49.87
2019-11-24 | 15:54 | 49.87
2019-11-24 | 15:54 | 49.869
2019-11-24 | 15:54 | 49.868
2019-11-24 | 15:54 | 49.867
2019-11-24 | 15:54 | 49.864
2019-11-24 | 15:54 | 49.863
2019-11-24 | 15:54 | 49.861
2019-11-24 | 15:54 | 49.858
2019-11-24 | 15:54 | 49.857
2019-11-24 | 15:54 | 49.857
2019-11-24 | 15:54 | 49.856
2019-11-24 | 15:54 | 49.856
2019-11-24 | 15:54 | 49.858
2019-11-24 | 15:54 | 49.859
2019-11-24 | 15:54 | 49.861
2019-11-24 | 15:54 | 49.862
2019-11-24 | 15:54 | 49.863
2019-11-24 | 15:54 | 49.865
2019-11-24 | 15:54 | 49.868
2019-11-24 | 15:54 | 49.87
2019-11-24 | 15:54 | 49.87
2019-11-24 | 15:54 | 49.87
2019-11-24 | 15:54 | 49.869
2019-11-24 | 15:54 | 49.868
2019-11-24 | 15:54 | 49.867
2019-11-24 | 15:54 | 49.864
2019-11-24 | 15:54 | 49.862
2019-11-24 | 15:54 | 49.861
2019-11-24 | 15:54 | 49.86
2019-11-24 | 15:54 | 49.857
2019-11-24 | 15:55 | 49.856
2019-11-24 | 15:55 | 49.856
2019-11-24 | 15:55 | 49.855
2019-11-24 | 15:55 | 49.854
2019-11-24 | 15:55 | 49.855
2019-11-24 | 15:55 | 49.853
2019-11-24 | 15:55 | 49.857
2019-11-24 | 15:55 | 49.858
2019-11-24 | 15:55 | 49.858
2019-11-24 | 15:55 | 49.859
2019-11-24 | 15:55 | 49.859
2019-11-24 | 15:55 | 49.858
2019-11-24 | 15:55 | 49.857
2019-11-24 | 15:55 | 49.855
2019-11-24 | 15:55 | 49.855
2019-11-24 | 15:55 | 49.856
2019-11-24 | 15:55 | 49.853
2019-11-24 | 15:55 | 49.853
2019-11-24 | 15:55 | 49.851
2019-11-24 | 15:55 | 49.851
2019-11-24 | 15:55 | 49.852
2019-11-24 | 15:55 | 49.85
2019-11-24 | 15:55 | 49.846
2019-11-24 | 15:55 | 49.844
2019-11-24 | 15:55 | 49.842
2019-11-24 | 15:55 | 49.839
2019-11-24 | 15:55 | 49.838
2019-11-24 | 15:55 | 49.837
2019-11-24 | 15:55 | 49.835
2019-11-24 | 15:55 | 49.832
2019-11-24 | 15:55 | 49.831
2019-11-24 | 15:55 | 49.829
2019-11-24 | 15:55 | 49.827
2019-11-24 | 15:55 | 49.826
2019-11-24 | 15:55 | 49.825
2019-11-24 | 15:55 | 49.826
2019-11-24 | 15:55 | 49.827
2019-11-24 | 15:55 | 49.828
2019-11-24 | 15:55 | 49.83
2019-11-24 | 15:55 | 49.831
2019-11-24 | 15:55 | 49.833
2019-11-24 | 15:55 | 49.836
2019-11-24 | 15:55 | 49.84
2019-11-24 | 15:55 | 49.839
2019-11-24 | 15:55 | 49.841
2019-11-24 | 15:55 | 49.843
2019-11-24 | 15:55 | 49.845
2019-11-24 | 15:55 | 49.848
2019-11-24 | 15:55 | 49.853
2019-11-24 | 15:55 | 49.86
2019-11-24 | 15:55 | 49.867
2019-11-24 | 15:55 | 49.873
2019-11-24 | 15:55 | 49.878
2019-11-24 | 15:55 | 49.881
2019-11-24 | 15:55 | 49.883
2019-11-24 | 15:55 | 49.888
2019-11-24 | 15:55 | 49.89
2019-11-24 | 15:55 | 49.892
2019-11-24 | 15:55 | 49.896
2019-11-24 | 15:56 | 49.896
2019-11-24 | 15:56 | 49.896
2019-11-24 | 15:56 | 49.898
2019-11-24 | 15:56 | 49.901
2019-11-24 | 15:56 | 49.903
2019-11-24 | 15:56 | 49.906
2019-11-24 | 15:56 | 49.91
2019-11-24 | 15:56 | 49.912
2019-11-24 | 15:56 | 49.916
2019-11-24 | 15:56 | 49.919
2019-11-24 | 15:56 | 49.922
2019-11-24 | 15:56 | 49.924
2019-11-24 | 15:56 | 49.927
2019-11-24 | 15:56 | 49.93
2019-11-24 | 15:56 | 49.932
2019-11-24 | 15:56 | 49.933
2019-11-24 | 15:56 | 49.933
2019-11-24 | 15:56 | 49.937
2019-11-24 | 15:56 | 49.941
2019-11-24 | 15:56 | 49.944
2019-11-24 | 15:56 | 49.945
2019-11-24 | 15:56 | 49.946
2019-11-24 | 15:56 | 49.946
2019-11-24 | 15:56 | 49.947
2019-11-24 | 15:56 | 49.946
2019-11-24 | 15:56 | 49.944
2019-11-24 | 15:56 | 49.944
2019-11-24 | 15:56 | 49.943
2019-11-24 | 15:56 | 49.942
2019-11-24 | 15:56 | 49.943
2019-11-24 | 15:56 | 49.941
2019-11-24 | 15:56 | 49.939
2019-11-24 | 15:56 | 49.938
2019-11-24 | 15:56 | 49.937
2019-11-24 | 15:56 | 49.937
2019-11-24 | 15:56 | 49.936
2019-11-24 | 15:56 | 49.936
2019-11-24 | 15:56 | 49.934
2019-11-24 | 15:56 | 49.934
2019-11-24 | 15:56 | 49.936
2019-11-24 | 15:56 | 49.936
2019-11-24 | 15:56 | 49.936
2019-11-24 | 15:56 | 49.935
2019-11-24 | 15:56 | 49.936
2019-11-24 | 15:56 | 49.936
2019-11-24 | 15:56 | 49.936
2019-11-24 | 15:56 | 49.936
2019-11-24 | 15:56 | 49.936
2019-11-24 | 15:56 | 49.935
2019-11-24 | 15:56 | 49.936
2019-11-24 | 15:56 | 49.938
2019-11-24 | 15:56 | 49.937
2019-11-24 | 15:56 | 49.936
2019-11-24 | 15:56 | 49.934
2019-11-24 | 15:56 | 49.935
2019-11-24 | 15:56 | 49.937
2019-11-24 | 15:56 | 49.937
2019-11-24 | 15:56 | 49.938
2019-11-24 | 15:56 | 49.941
2019-11-24 | 15:56 | 49.943
2019-11-24 | 15:56 | 49.945
2019-11-24 | 15:57 | 49.948
2019-11-24 | 15:57 | 49.95
2019-11-24 | 15:57 | 49.951
2019-11-24 | 15:57 | 49.951
2019-11-24 | 15:57 | 49.954
2019-11-24 | 15:57 | 49.955
2019-11-24 | 15:57 | 49.956
2019-11-24 | 15:57 | 49.955
2019-11-24 | 15:57 | 49.955
2019-11-24 | 15:57 | 49.953
2019-11-24 | 15:57 | 49.949
2019-11-24 | 15:57 | 49.946
2019-11-24 | 15:57 | 49.944
2019-11-24 | 15:57 | 49.942
2019-11-24 | 15:57 | 49.942
2019-11-24 | 15:57 | 49.941
2019-11-24 | 15:57 | 49.94
2019-11-24 | 15:57 | 49.94
2019-11-24 | 15:57 | 49.94
2019-11-24 | 15:57 | 49.94
2019-11-24 | 15:57 | 49.939
2019-11-24 | 15:57 | 49.938
2019-11-24 | 15:57 | 49.939
2019-11-24 | 15:57 | 49.939
2019-11-24 | 15:57 | 49.94
2019-11-24 | 15:57 | 49.942
2019-11-24 | 15:57 | 49.945
2019-11-24 | 15:57 | 49.948
2019-11-24 | 15:57 | 49.95
2019-11-24 | 15:57 | 49.949
2019-11-24 | 15:57 | 49.947
2019-11-24 | 15:57 | 49.948
2019-11-24 | 15:57 | 49.945
2019-11-24 | 15:57 | 49.943
2019-11-24 | 15:57 | 49.94
2019-11-24 | 15:57 | 49.938
2019-11-24 | 15:57 | 49.936
2019-11-24 | 15:57 | 49.933
2019-11-24 | 15:57 | 49.935
2019-11-24 | 15:57 | 49.935
2019-11-24 | 15:57 | 49.935
2019-11-24 | 15:57 | 49.935
2019-11-24 | 15:57 | 49.933
2019-11-24 | 15:57 | 49.934
2019-11-24 | 15:57 | 49.933
2019-11-24 | 15:57 | 49.933
2019-11-24 | 15:57 | 49.933
2019-11-24 | 15:57 | 49.933
2019-11-24 | 15:57 | 49.931
2019-11-24 | 15:57 | 49.93
2019-11-24 | 15:57 | 49.93
2019-11-24 | 15:57 | 49.928
2019-11-24 | 15:57 | 49.929
2019-11-24 | 15:57 | 49.929
2019-11-24 | 15:57 | 49.929
2019-11-24 | 15:57 | 49.929
2019-11-24 | 15:57 | 49.928
2019-11-24 | 15:57 | 49.928
2019-11-24 | 15:57 | 49.93
2019-11-24 | 15:58 | 49.932
2019-11-24 | 15:58 | 49.935
2019-11-24 | 15:58 | 49.94
2019-11-24 | 15:58 | 49.945
2019-11-24 | 15:58 | 49.949
2019-11-24 | 15:58 | 49.952
2019-11-24 | 15:58 | 49.955
2019-11-24 | 15:58 | 49.957
2019-11-24 | 15:58 | 49.959
2019-11-24 | 15:58 | 49.96
2019-11-24 | 15:58 | 49.961
2019-11-24 | 15:58 | 49.961
2019-11-24 | 15:58 | 49.963
2019-11-24 | 15:58 | 49.963
2019-11-24 | 15:58 | 49.962
2019-11-24 | 15:58 | 49.96
2019-11-24 | 15:58 | 49.96
2019-11-24 | 15:58 | 49.958
2019-11-24 | 15:58 | 49.957
2019-11-24 | 15:58 | 49.956
2019-11-24 | 15:58 | 49.954
2019-11-24 | 15:58 | 49.955
2019-11-24 | 15:58 | 49.954
2019-11-24 | 15:58 | 49.955
2019-11-24 | 15:58 | 49.954
2019-11-24 | 15:58 | 49.952
2019-11-24 | 15:58 | 49.951
2019-11-24 | 15:58 | 49.951
2019-11-24 | 15:58 | 49.95
2019-11-24 | 15:58 | 49.947
2019-11-24 | 15:58 | 49.946
2019-11-24 | 15:58 | 49.947
2019-11-24 | 15:58 | 49.946
2019-11-24 | 15:58 | 49.947
2019-11-24 | 15:58 | 49.948
2019-11-24 | 15:58 | 49.947
2019-11-24 | 15:58 | 49.946
2019-11-24 | 15:58 | 49.947
2019-11-24 | 15:58 | 49.949
2019-11-24 | 15:58 | 49.947
2019-11-24 | 15:58 | 49.948
2019-11-24 | 15:58 | 49.949
2019-11-24 | 15:58 | 49.949
2019-11-24 | 15:58 | 49.949
2019-11-24 | 15:58 | 49.949
2019-11-24 | 15:58 | 49.949
2019-11-24 | 15:58 | 49.95
2019-11-24 | 15:58 | 49.949
2019-11-24 | 15:58 | 49.949
2019-11-24 | 15:58 | 49.95
2019-11-24 | 15:58 | 49.949
2019-11-24 | 15:58 | 49.95
2019-11-24 | 15:58 | 49.949
2019-11-24 | 15:58 | 49.949
2019-11-24 | 15:58 | 49.949
2019-11-24 | 15:58 | 49.95
2019-11-24 | 15:58 | 49.948
2019-11-24 | 15:58 | 49.945
2019-11-24 | 15:58 | 49.943
2019-11-24 | 15:58 | 49.94
2019-11-24 | 15:58 | 49.937
2019-11-24 | 15:59 | 49.935
2019-11-24 | 15:59 | 49.932
2019-11-24 | 15:59 | 49.932
2019-11-24 | 15:59 | 49.932
2019-11-24 | 15:59 | 49.931
2019-11-24 | 15:59 | 49.931
2019-11-24 | 15:59 | 49.932
2019-11-24 | 15:59 | 49.933
2019-11-24 | 15:59 | 49.934
2019-11-24 | 15:59 | 49.935
2019-11-24 | 15:59 | 49.934
2019-11-24 | 15:59 | 49.937
2019-11-24 | 15:59 | 49.937
2019-11-24 | 15:59 | 49.938
2019-11-24 | 15:59 | 49.937
2019-11-24 | 15:59 | 49.936
2019-11-24 | 15:59 | 49.937
2019-11-24 | 15:59 | 49.938
2019-11-24 | 15:59 | 49.939
2019-11-24 | 15:59 | 49.94
2019-11-24 | 15:59 | 49.937
2019-11-24 | 15:59 | 49.936
2019-11-24 | 15:59 | 49.937
2019-11-24 | 15:59 | 49.937
2019-11-24 | 15:59 | 49.937
2019-11-24 | 15:59 | 49.937
2019-11-24 | 15:59 | 49.937
2019-11-24 | 15:59 | 49.938
2019-11-24 | 15:59 | 49.939
2019-11-24 | 15:59 | 49.937
2019-11-24 | 15:59 | 49.934
2019-11-24 | 15:59 | 49.933
2019-11-24 | 15:59 | 49.932
2019-11-24 | 15:59 | 49.933
2019-11-24 | 15:59 | 49.934
2019-11-24 | 15:59 | 49.938
2019-11-24 | 15:59 | 49.942
2019-11-24 | 15:59 | 49.946
2019-11-24 | 15:59 | 49.947
2019-11-24 | 15:59 | 49.947
2019-11-24 | 15:59 | 49.947
2019-11-24 | 15:59 | 49.949
2019-11-24 | 15:59 | 49.947
2019-11-24 | 15:59 | 49.946
2019-11-24 | 15:59 | 49.944
2019-11-24 | 15:59 | 49.943
2019-11-24 | 15:59 | 49.942
2019-11-24 | 15:59 | 49.941
2019-11-24 | 15:59 | 49.943
2019-11-24 | 15:59 | 49.944
2019-11-24 | 15:59 | 49.946
2019-11-24 | 15:59 | 49.948
2019-11-24 | 15:59 | 49.948
2019-11-24 | 15:59 | 49.945
2019-11-24 | 15:59 | 49.945
2019-11-24 | 15:59 | 49.944
2019-11-24 | 15:59 | 49.941
2019-11-24 | 15:59 | 49.939
2019-11-24 | 15:59 | 49.936
2019-11-24 | 16:00 | 49.937
2019-11-24 | 16:00 | 49.936
2019-11-24 | 16:00 | 49.933
2019-11-24 | 16:00 | 49.932
2019-11-24 | 16:00 | 49.932
2019-11-24 | 16:00 | 49.934
2019-11-24 | 16:00 | 49.934
2019-11-24 | 16:00 | 49.936
2019-11-24 | 16:00 | 49.937
2019-11-24 | 16:00 | 49.941
2019-11-24 | 16:00 | 49.943
2019-11-24 | 16:00 | 49.945
2019-11-24 | 16:00 | 49.948
2019-11-24 | 16:00 | 49.949
2019-11-24 | 16:00 | 49.953
2019-11-24 | 16:00 | 49.955
2019-11-24 | 16:00 | 49.955
2019-11-24 | 16:00 | 49.954
2019-11-24 | 16:00 | 49.954
2019-11-24 | 16:00 | 49.955
2019-11-24 | 16:00 | 49.956
2019-11-24 | 16:00 | 49.957
2019-11-24 | 16:00 | 49.958
2019-11-24 | 16:00 | 49.959
2019-11-24 | 16:00 | 49.957
2019-11-24 | 16:00 | 49.958
2019-11-24 | 16:00 | 49.955
2019-11-24 | 16:00 | 49.954
2019-11-24 | 16:00 | 49.953
2019-11-24 | 16:00 | 49.955
2019-11-24 | 16:00 | 49.953
2019-11-24 | 16:00 | 49.952
2019-11-24 | 16:00 | 49.95
2019-11-24 | 16:00 | 49.947
2019-11-24 | 16:00 | 49.946
2019-11-24 | 16:00 | 49.944
2019-11-24 | 16:00 | 49.946
2019-11-24 | 16:00 | 49.945
2019-11-24 | 16:00 | 49.944
2019-11-24 | 16:00 | 49.948
2019-11-24 | 16:00 | 49.95
2019-11-24 | 16:00 | 49.952
2019-11-24 | 16:00 | 49.953
2019-11-24 | 16:00 | 49.955
2019-11-24 | 16:00 | 49.956
2019-11-24 | 16:00 | 49.958
2019-11-24 | 16:00 | 49.958
2019-11-24 | 16:00 | 49.96
2019-11-24 | 16:00 | 49.96
2019-11-24 | 16:00 | 49.96
2019-11-24 | 16:00 | 49.959
2019-11-24 | 16:00 | 49.958
2019-11-24 | 16:00 | 49.959
2019-11-24 | 16:00 | 49.958
2019-11-24 | 16:00 | 49.957
2019-11-24 | 16:00 | 49.957
2019-11-24 | 16:00 | 49.955
2019-11-24 | 16:00 | 49.954
2019-11-24 | 16:00 | 49.952
2019-11-24 | 16:00 | 49.951
2019-11-24 | 16:00 | 49.949
2019-11-24 | 16:01 | 49.947
2019-11-24 | 16:01 | 49.946
2019-11-24 | 16:01 | 49.944
2019-11-24 | 16:01 | 49.944
2019-11-24 | 16:01 | 49.943
2019-11-24 | 16:01 | 49.941
2019-11-24 | 16:01 | 49.941
2019-11-24 | 16:01 | 49.942
2019-11-24 | 16:01 | 49.94
2019-11-24 | 16:01 | 49.941
2019-11-24 | 16:01 | 49.94
2019-11-24 | 16:01 | 49.938
2019-11-24 | 16:01 | 49.939
2019-11-24 | 16:01 | 49.937
2019-11-24 | 16:01 | 49.937
2019-11-24 | 16:01 | 49.938
2019-11-24 | 16:01 | 49.938
2019-11-24 | 16:01 | 49.94
2019-11-24 | 16:01 | 49.938
2019-11-24 | 16:01 | 49.939
2019-11-24 | 16:01 | 49.938
2019-11-24 | 16:01 | 49.936
2019-11-24 | 16:01 | 49.933
2019-11-24 | 16:01 | 49.934
2019-11-24 | 16:01 | 49.934
2019-11-24 | 16:01 | 49.933
2019-11-24 | 16:01 | 49.932
2019-11-24 | 16:01 | 49.933
2019-11-24 | 16:01 | 49.933
2019-11-24 | 16:01 | 49.933
2019-11-24 | 16:01 | 49.932
2019-11-24 | 16:01 | 49.932
2019-11-24 | 16:01 | 49.932
2019-11-24 | 16:01 | 49.934
2019-11-24 | 16:01 | 49.93
2019-11-24 | 16:01 | 49.927
2019-11-24 | 16:01 | 49.925
2019-11-24 | 16:01 | 49.923
2019-11-24 | 16:01 | 49.921
2019-11-24 | 16:01 | 49.919
2019-11-24 | 16:01 | 49.919
2019-11-24 | 16:01 | 49.916
2019-11-24 | 16:01 | 49.917
2019-11-24 | 16:01 | 49.916
2019-11-24 | 16:01 | 49.916
2019-11-24 | 16:01 | 49.917
2019-11-24 | 16:01 | 49.916
2019-11-24 | 16:01 | 49.917
2019-11-24 | 16:01 | 49.916
2019-11-24 | 16:01 | 49.92
2019-11-24 | 16:01 | 49.923
2019-11-24 | 16:01 | 49.925
2019-11-24 | 16:01 | 49.928
2019-11-24 | 16:01 | 49.929
2019-11-24 | 16:01 | 49.929
2019-11-24 | 16:01 | 49.928
2019-11-24 | 16:01 | 49.928
2019-11-24 | 16:01 | 49.925
2019-11-24 | 16:01 | 49.922
2019-11-24 | 16:01 | 49.919
2019-11-24 | 16:02 | 49.917
2019-11-24 | 16:02 | 49.915
2019-11-24 | 16:02 | 49.914
2019-11-24 | 16:02 | 49.914
2019-11-24 | 16:02 | 49.916
2019-11-24 | 16:02 | 49.918
2019-11-24 | 16:02 | 49.92
2019-11-24 | 16:02 | 49.922
2019-11-24 | 16:02 | 49.924
2019-11-24 | 16:02 | 49.926
2019-11-24 | 16:02 | 49.924
2019-11-24 | 16:02 | 49.923
2019-11-24 | 16:02 | 49.921
2019-11-24 | 16:02 | 49.919
2019-11-24 | 16:02 | 49.918
2019-11-24 | 16:02 | 49.918
2019-11-24 | 16:02 | 49.918
2019-11-24 | 16:02 | 49.92
2019-11-24 | 16:02 | 49.921
2019-11-24 | 16:02 | 49.921
2019-11-24 | 16:02 | 49.925
2019-11-24 | 16:02 | 49.927
2019-11-24 | 16:02 | 49.929
2019-11-24 | 16:02 | 49.928
2019-11-24 | 16:02 | 49.93
2019-11-24 | 16:02 | 49.931
2019-11-24 | 16:02 | 49.933
2019-11-24 | 16:02 | 49.935
2019-11-24 | 16:02 | 49.935
2019-11-24 | 16:02 | 49.936
2019-11-24 | 16:02 | 49.937
2019-11-24 | 16:02 | 49.936
2019-11-24 | 16:02 | 49.936
2019-11-24 | 16:02 | 49.936
2019-11-24 | 16:02 | 49.936
2019-11-24 | 16:02 | 49.935
2019-11-24 | 16:02 | 49.936
2019-11-24 | 16:02 | 49.935
2019-11-24 | 16:02 | 49.933
2019-11-24 | 16:02 | 49.931
2019-11-24 | 16:02 | 49.929
2019-11-24 | 16:02 | 49.928
2019-11-24 | 16:02 | 49.928
2019-11-24 | 16:02 | 49.93
2019-11-24 | 16:02 | 49.932
2019-11-24 | 16:02 | 49.933
2019-11-24 | 16:02 | 49.937
2019-11-24 | 16:02 | 49.94
2019-11-24 | 16:02 | 49.943
2019-11-24 | 16:02 | 49.945
2019-11-24 | 16:02 | 49.945
2019-11-24 | 16:02 | 49.947
2019-11-24 | 16:02 | 49.946
2019-11-24 | 16:02 | 49.947
2019-11-24 | 16:02 | 49.948
2019-11-24 | 16:02 | 49.948
2019-11-24 | 16:02 | 49.949
2019-11-24 | 16:02 | 49.949
2019-11-24 | 16:02 | 49.95
2019-11-24 | 16:02 | 49.948
2019-11-24 | 16:03 | 49.947
2019-11-24 | 16:03 | 49.946
2019-11-24 | 16:03 | 49.947
2019-11-24 | 16:03 | 49.945
2019-11-24 | 16:03 | 49.944
2019-11-24 | 16:03 | 49.942
2019-11-24 | 16:03 | 49.942
2019-11-24 | 16:03 | 49.943
2019-11-24 | 16:03 | 49.944
2019-11-24 | 16:03 | 49.943
2019-11-24 | 16:03 | 49.943
2019-11-24 | 16:03 | 49.943
2019-11-24 | 16:03 | 49.943
2019-11-24 | 16:03 | 49.942
2019-11-24 | 16:03 | 49.941
2019-11-24 | 16:03 | 49.94
2019-11-24 | 16:03 | 49.939
2019-11-24 | 16:03 | 49.937
2019-11-24 | 16:03 | 49.934
2019-11-24 | 16:03 | 49.932
2019-11-24 | 16:03 | 49.929
2019-11-24 | 16:03 | 49.927
2019-11-24 | 16:03 | 49.925
2019-11-24 | 16:03 | 49.923
2019-11-24 | 16:03 | 49.922
2019-11-24 | 16:03 | 49.92
2019-11-24 | 16:03 | 49.918
2019-11-24 | 16:03 | 49.917
2019-11-24 | 16:03 | 49.916
2019-11-24 | 16:03 | 49.915
2019-11-24 | 16:03 | 49.915
2019-11-24 | 16:03 | 49.914
2019-11-24 | 16:03 | 49.915
2019-11-24 | 16:03 | 49.917
2019-11-24 | 16:03 | 49.919
2019-11-24 | 16:03 | 49.921
2019-11-24 | 16:03 | 49.927
2019-11-24 | 16:03 | 49.932
2019-11-24 | 16:03 | 49.94
2019-11-24 | 16:03 | 49.946
2019-11-24 | 16:03 | 49.951
2019-11-24 | 16:03 | 49.956
2019-11-24 | 16:03 | 49.958
2019-11-24 | 16:03 | 49.959
2019-11-24 | 16:03 | 49.958
2019-11-24 | 16:03 | 49.958
2019-11-24 | 16:03 | 49.958
2019-11-24 | 16:03 | 49.959
2019-11-24 | 16:03 | 49.96
2019-11-24 | 16:03 | 49.961
2019-11-24 | 16:03 | 49.963
2019-11-24 | 16:03 | 49.965
2019-11-24 | 16:03 | 49.964
2019-11-24 | 16:03 | 49.963
2019-11-24 | 16:03 | 49.962
2019-11-24 | 16:03 | 49.961
2019-11-24 | 16:03 | 49.961
2019-11-24 | 16:03 | 49.961
2019-11-24 | 16:03 | 49.962
2019-11-24 | 16:04 | 49.966
2019-11-24 | 16:04 | 49.967
2019-11-24 | 16:04 | 49.969
2019-11-24 | 16:04 | 49.967
2019-11-24 | 16:04 | 49.969
2019-11-24 | 16:04 | 49.969
2019-11-24 | 16:04 | 49.97
2019-11-24 | 16:04 | 49.967
2019-11-24 | 16:04 | 49.965
2019-11-24 | 16:04 | 49.963
2019-11-24 | 16:04 | 49.96
2019-11-24 | 16:04 | 49.955
2019-11-24 | 16:04 | 49.953
2019-11-24 | 16:04 | 49.949
2019-11-24 | 16:04 | 49.95
2019-11-24 | 16:04 | 49.952
2019-11-24 | 16:04 | 49.954
2019-11-24 | 16:04 | 49.953
2019-11-24 | 16:04 | 49.954
2019-11-24 | 16:04 | 49.956
2019-11-24 | 16:04 | 49.959
2019-11-24 | 16:04 | 49.959
2019-11-24 | 16:04 | 49.959
2019-11-24 | 16:04 | 49.96
2019-11-24 | 16:04 | 49.96
2019-11-24 | 16:04 | 49.959
2019-11-24 | 16:04 | 49.96
2019-11-24 | 16:04 | 49.962
2019-11-24 | 16:04 | 49.96
2019-11-24 | 16:04 | 49.96
2019-11-24 | 16:04 | 49.961
2019-11-24 | 16:04 | 49.961
2019-11-24 | 16:04 | 49.96
2019-11-24 | 16:04 | 49.96
2019-11-24 | 16:04 | 49.96
2019-11-24 | 16:04 | 49.96
2019-11-24 | 16:04 | 49.962
2019-11-24 | 16:04 | 49.963
2019-11-24 | 16:04 | 49.964
2019-11-24 | 16:04 | 49.967
2019-11-24 | 16:04 | 49.969
2019-11-24 | 16:04 | 49.97
2019-11-24 | 16:04 | 49.972
2019-11-24 | 16:04 | 49.975
2019-11-24 | 16:04 | 49.976
2019-11-24 | 16:04 | 49.98
2019-11-24 | 16:04 | 49.982
2019-11-24 | 16:04 | 49.984
2019-11-24 | 16:04 | 49.985
2019-11-24 | 16:04 | 49.984
2019-11-24 | 16:04 | 49.984
2019-11-24 | 16:04 | 49.983
2019-11-24 | 16:04 | 49.981
2019-11-24 | 16:04 | 49.98
2019-11-24 | 16:04 | 49.978
2019-11-24 | 16:04 | 49.976
2019-11-24 | 16:04 | 49.972
2019-11-24 | 16:04 | 49.968
2019-11-24 | 16:04 | 49.963
2019-11-24 | 16:04 | 49.962
2019-11-24 | 16:04 | 49.958
2019-11-24 | 16:05 | 49.954
2019-11-24 | 16:05 | 49.952
2019-11-24 | 16:05 | 49.951
2019-11-24 | 16:05 | 49.951
2019-11-24 | 16:05 | 49.951
2019-11-24 | 16:05 | 49.953
2019-11-24 | 16:05 | 49.955
2019-11-24 | 16:05 | 49.955
2019-11-24 | 16:05 | 49.956
2019-11-24 | 16:05 | 49.958
2019-11-24 | 16:05 | 49.957
2019-11-24 | 16:05 | 49.958
2019-11-24 | 16:05 | 49.959
2019-11-24 | 16:05 | 49.961
2019-11-24 | 16:05 | 49.963
2019-11-24 | 16:05 | 49.961
2019-11-24 | 16:05 | 49.957
2019-11-24 | 16:05 | 49.955
2019-11-24 | 16:05 | 49.955
2019-11-24 | 16:05 | 49.955
2019-11-24 | 16:05 | 49.953
2019-11-24 | 16:05 | 49.951
2019-11-24 | 16:05 | 49.949
2019-11-24 | 16:05 | 49.946
2019-11-24 | 16:05 | 49.943
2019-11-24 | 16:05 | 49.94
2019-11-24 | 16:05 | 49.938
2019-11-24 | 16:05 | 49.935
2019-11-24 | 16:05 | 49.932
2019-11-24 | 16:05 | 49.929
2019-11-24 | 16:05 | 49.926
2019-11-24 | 16:05 | 49.924
2019-11-24 | 16:05 | 49.922
2019-11-24 | 16:05 | 49.921
2019-11-24 | 16:05 | 49.921
2019-11-24 | 16:05 | 49.919
2019-11-24 | 16:05 | 49.918
2019-11-24 | 16:05 | 49.919
2019-11-24 | 16:05 | 49.918
2019-11-24 | 16:05 | 49.919
2019-11-24 | 16:05 | 49.918
2019-11-24 | 16:05 | 49.917
2019-11-24 | 16:05 | 49.917
2019-11-24 | 16:05 | 49.914
2019-11-24 | 16:05 | 49.913
2019-11-24 | 16:05 | 49.909
2019-11-24 | 16:05 | 49.909
2019-11-24 | 16:05 | 49.908
2019-11-24 | 16:05 | 49.908
2019-11-24 | 16:05 | 49.907
2019-11-24 | 16:05 | 49.908
2019-11-24 | 16:05 | 49.908
2019-11-24 | 16:05 | 49.908
2019-11-24 | 16:05 | 49.91
2019-11-24 | 16:05 | 49.911
2019-11-24 | 16:05 | 49.912
2019-11-24 | 16:05 | 49.912
2019-11-24 | 16:05 | 49.91
2019-11-24 | 16:05 | 49.912
2019-11-24 | 16:05 | 49.915
2019-11-24 | 16:06 | 49.914
2019-11-24 | 16:06 | 49.914
2019-11-24 | 16:06 | 49.916
2019-11-24 | 16:06 | 49.918
2019-11-24 | 16:06 | 49.919
2019-11-24 | 16:06 | 49.918
2019-11-24 | 16:06 | 49.917
2019-11-24 | 16:06 | 49.917
2019-11-24 | 16:06 | 49.917
2019-11-24 | 16:06 | 49.914
2019-11-24 | 16:06 | 49.914
2019-11-24 | 16:06 | 49.913
2019-11-24 | 16:06 | 49.911
2019-11-24 | 16:06 | 49.909
2019-11-24 | 16:06 | 49.908
2019-11-24 | 16:06 | 49.907
2019-11-24 | 16:06 | 49.904
2019-11-24 | 16:06 | 49.901
2019-11-24 | 16:06 | 49.898
2019-11-24 | 16:06 | 49.897
2019-11-24 | 16:06 | 49.896
2019-11-24 | 16:06 | 49.895
2019-11-24 | 16:06 | 49.894
2019-11-24 | 16:06 | 49.897
2019-11-24 | 16:06 | 49.897
2019-11-24 | 16:06 | 49.897
2019-11-24 | 16:06 | 49.898
2019-11-24 | 16:06 | 49.898
2019-11-24 | 16:06 | 49.898
2019-11-24 | 16:06 | 49.897
2019-11-24 | 16:06 | 49.894
2019-11-24 | 16:06 | 49.891
2019-11-24 | 16:06 | 49.888
2019-11-24 | 16:06 | 49.887
2019-11-24 | 16:06 | 49.885
2019-11-24 | 16:06 | 49.887
2019-11-24 | 16:06 | 49.89
2019-11-24 | 16:06 | 49.893
2019-11-24 | 16:06 | 49.896
2019-11-24 | 16:06 | 49.9
2019-11-24 | 16:06 | 49.903
2019-11-24 | 16:06 | 49.906
2019-11-24 | 16:06 | 49.908
2019-11-24 | 16:06 | 49.909
2019-11-24 | 16:06 | 49.913
2019-11-24 | 16:06 | 49.917
2019-11-24 | 16:06 | 49.92
2019-11-24 | 16:06 | 49.92
2019-11-24 | 16:06 | 49.921
2019-11-24 | 16:06 | 49.924
2019-11-24 | 16:06 | 49.924
2019-11-24 | 16:06 | 49.925
2019-11-24 | 16:06 | 49.926
2019-11-24 | 16:06 | 49.925
2019-11-24 | 16:06 | 49.925
2019-11-24 | 16:06 | 49.926
2019-11-24 | 16:06 | 49.928
2019-11-24 | 16:06 | 49.928
2019-11-24 | 16:06 | 49.927
2019-11-24 | 16:06 | 49.927
2019-11-24 | 16:07 | 49.927
2019-11-24 | 16:07 | 49.926
2019-11-24 | 16:07 | 49.926
2019-11-24 | 16:07 | 49.926
2019-11-24 | 16:07 | 49.925
2019-11-24 | 16:07 | 49.924
2019-11-24 | 16:07 | 49.923
2019-11-24 | 16:07 | 49.921
2019-11-24 | 16:07 | 49.923
2019-11-24 | 16:07 | 49.924
2019-11-24 | 16:07 | 49.923
2019-11-24 | 16:07 | 49.923
2019-11-24 | 16:07 | 49.925
2019-11-24 | 16:07 | 49.923
2019-11-24 | 16:07 | 49.923
2019-11-24 | 16:07 | 49.925
2019-11-24 | 16:07 | 49.926
2019-11-24 | 16:07 | 49.928
2019-11-24 | 16:07 | 49.927
2019-11-24 | 16:07 | 49.929
2019-11-24 | 16:07 | 49.929
2019-11-24 | 16:07 | 49.931
2019-11-24 | 16:07 | 49.932
2019-11-24 | 16:07 | 49.933
2019-11-24 | 16:07 | 49.934
2019-11-24 | 16:07 | 49.935
2019-11-24 | 16:07 | 49.933
2019-11-24 | 16:07 | 49.933
2019-11-24 | 16:07 | 49.931
2019-11-24 | 16:07 | 49.932
2019-11-24 | 16:07 | 49.933
2019-11-24 | 16:07 | 49.931
2019-11-24 | 16:07 | 49.932
2019-11-24 | 16:07 | 49.932
2019-11-24 | 16:07 | 49.931
2019-11-24 | 16:07 | 49.928
2019-11-24 | 16:07 | 49.928
2019-11-24 | 16:07 | 49.925
2019-11-24 | 16:07 | 49.926
2019-11-24 | 16:07 | 49.925
2019-11-24 | 16:07 | 49.925
2019-11-24 | 16:07 | 49.922
2019-11-24 | 16:07 | 49.918
2019-11-24 | 16:07 | 49.916
2019-11-24 | 16:07 | 49.913
2019-11-24 | 16:07 | 49.912
2019-11-24 | 16:07 | 49.909
2019-11-24 | 16:07 | 49.908
2019-11-24 | 16:07 | 49.909
2019-11-24 | 16:07 | 49.908
2019-11-24 | 16:07 | 49.908
2019-11-24 | 16:07 | 49.909
2019-11-24 | 16:07 | 49.908
2019-11-24 | 16:07 | 49.91
2019-11-24 | 16:07 | 49.909
2019-11-24 | 16:07 | 49.911
2019-11-24 | 16:07 | 49.91
2019-11-24 | 16:07 | 49.91
2019-11-24 | 16:07 | 49.912
2019-11-24 | 16:08 | 49.913
2019-11-24 | 16:08 | 49.912
2019-11-24 | 16:08 | 49.911
2019-11-24 | 16:08 | 49.91
2019-11-24 | 16:08 | 49.91
2019-11-24 | 16:08 | 49.91
2019-11-24 | 16:08 | 49.909
2019-11-24 | 16:08 | 49.906
2019-11-24 | 16:08 | 49.905
2019-11-24 | 16:08 | 49.904
2019-11-24 | 16:08 | 49.903
2019-11-24 | 16:08 | 49.902
2019-11-24 | 16:08 | 49.898
2019-11-24 | 16:08 | 49.894
2019-11-24 | 16:08 | 49.893
2019-11-24 | 16:08 | 49.893
2019-11-24 | 16:08 | 49.897
2019-11-24 | 16:08 | 49.902
2019-11-24 | 16:08 | 49.905
2019-11-24 | 16:08 | 49.908
2019-11-24 | 16:08 | 49.91
2019-11-24 | 16:08 | 49.913
2019-11-24 | 16:08 | 49.917
2019-11-24 | 16:08 | 49.914
2019-11-24 | 16:08 | 49.912
2019-11-24 | 16:08 | 49.91
2019-11-24 | 16:08 | 49.907
2019-11-24 | 16:08 | 49.903
2019-11-24 | 16:08 | 49.9
2019-11-24 | 16:08 | 49.899
2019-11-24 | 16:08 | 49.898
2019-11-24 | 16:08 | 49.898
2019-11-24 | 16:08 | 49.899
2019-11-24 | 16:08 | 49.9
2019-11-24 | 16:08 | 49.903
2019-11-24 | 16:08 | 49.904
2019-11-24 | 16:08 | 49.905
2019-11-24 | 16:08 | 49.908
2019-11-24 | 16:08 | 49.909
2019-11-24 | 16:08 | 49.909
2019-11-24 | 16:08 | 49.909
2019-11-24 | 16:08 | 49.91
2019-11-24 | 16:08 | 49.911
2019-11-24 | 16:08 | 49.912
2019-11-24 | 16:08 | 49.913
2019-11-24 | 16:08 | 49.916
2019-11-24 | 16:08 | 49.917
2019-11-24 | 16:08 | 49.918
2019-11-24 | 16:08 | 49.916
2019-11-24 | 16:08 | 49.917
2019-11-24 | 16:08 | 49.916
2019-11-24 | 16:08 | 49.916
2019-11-24 | 16:08 | 49.914
2019-11-24 | 16:08 | 49.912
2019-11-24 | 16:08 | 49.909
2019-11-24 | 16:08 | 49.908
2019-11-24 | 16:08 | 49.908
2019-11-24 | 16:08 | 49.91
2019-11-24 | 16:08 | 49.913
2019-11-24 | 16:08 | 49.914
2019-11-24 | 16:08 | 49.917
2019-11-24 | 16:09 | 49.919
2019-11-24 | 16:09 | 49.922
2019-11-24 | 16:09 | 49.924
2019-11-24 | 16:09 | 49.928
2019-11-24 | 16:09 | 49.929
2019-11-24 | 16:09 | 49.93
2019-11-24 | 16:09 | 49.931
2019-11-24 | 16:09 | 49.932
2019-11-24 | 16:09 | 49.933
2019-11-24 | 16:09 | 49.935
2019-11-24 | 16:09 | 49.934
2019-11-24 | 16:09 | 49.933
2019-11-24 | 16:09 | 49.934
2019-11-24 | 16:09 | 49.934
2019-11-24 | 16:09 | 49.935
2019-11-24 | 16:09 | 49.935
2019-11-24 | 16:09 | 49.935
2019-11-24 | 16:09 | 49.935
2019-11-24 | 16:09 | 49.935
2019-11-24 | 16:09 | 49.936
2019-11-24 | 16:09 | 49.936
2019-11-24 | 16:09 | 49.936
2019-11-24 | 16:09 | 49.933
2019-11-24 | 16:09 | 49.932
2019-11-24 | 16:09 | 49.93
2019-11-24 | 16:09 | 49.928
2019-11-24 | 16:09 | 49.926
2019-11-24 | 16:09 | 49.922
2019-11-24 | 16:09 | 49.92
2019-11-24 | 16:09 | 49.917
2019-11-24 | 16:09 | 49.914
2019-11-24 | 16:09 | 49.914
2019-11-24 | 16:09 | 49.912
2019-11-24 | 16:09 | 49.913
2019-11-24 | 16:09 | 49.914
2019-11-24 | 16:09 | 49.913
2019-11-24 | 16:09 | 49.913
2019-11-24 | 16:09 | 49.913
2019-11-24 | 16:09 | 49.915
2019-11-24 | 16:09 | 49.914
2019-11-24 | 16:09 | 49.914
2019-11-24 | 16:09 | 49.911
2019-11-24 | 16:09 | 49.909
2019-11-24 | 16:09 | 49.908
2019-11-24 | 16:09 | 49.906
2019-11-24 | 16:09 | 49.905
2019-11-24 | 16:09 | 49.905
2019-11-24 | 16:09 | 49.905
2019-11-24 | 16:09 | 49.902
2019-11-24 | 16:09 | 49.9
2019-11-24 | 16:09 | 49.9
2019-11-24 | 16:09 | 49.898
2019-11-24 | 16:09 | 49.898
2019-11-24 | 16:09 | 49.899
2019-11-24 | 16:09 | 49.899
2019-11-24 | 16:09 | 49.9
2019-11-24 | 16:09 | 49.901
2019-11-24 | 16:09 | 49.902
2019-11-24 | 16:09 | 49.903
2019-11-24 | 16:10 | 49.904
2019-11-24 | 16:10 | 49.904
2019-11-24 | 16:10 | 49.905
2019-11-24 | 16:10 | 49.905
2019-11-24 | 16:10 | 49.906
2019-11-24 | 16:10 | 49.907
2019-11-24 | 16:10 | 49.907
2019-11-24 | 16:10 | 49.906
2019-11-24 | 16:10 | 49.907
2019-11-24 | 16:10 | 49.906
2019-11-24 | 16:10 | 49.906
2019-11-24 | 16:10 | 49.906
2019-11-24 | 16:10 | 49.905
2019-11-24 | 16:10 | 49.904
2019-11-24 | 16:10 | 49.903
2019-11-24 | 16:10 | 49.901
2019-11-24 | 16:10 | 49.899
2019-11-24 | 16:10 | 49.896
2019-11-24 | 16:10 | 49.895
2019-11-24 | 16:10 | 49.893
2019-11-24 | 16:10 | 49.89
2019-11-24 | 16:10 | 49.889
2019-11-24 | 16:10 | 49.887
2019-11-24 | 16:10 | 49.885
2019-11-24 | 16:10 | 49.885
2019-11-24 | 16:10 | 49.884
2019-11-24 | 16:10 | 49.881
2019-11-24 | 16:10 | 49.88
2019-11-24 | 16:10 | 49.88
2019-11-24 | 16:10 | 49.881
2019-11-24 | 16:10 | 49.884
2019-11-24 | 16:10 | 49.884
2019-11-24 | 16:10 | 49.884
2019-11-24 | 16:10 | 49.884
2019-11-24 | 16:10 | 49.884
2019-11-24 | 16:10 | 49.884
2019-11-24 | 16:10 | 49.884
2019-11-24 | 16:10 | 49.882
2019-11-24 | 16:10 | 49.881
2019-11-24 | 16:10 | 49.878
2019-11-24 | 16:10 | 49.877
2019-11-24 | 16:10 | 49.875
2019-11-24 | 16:10 | 49.873
2019-11-24 | 16:10 | 49.872
2019-11-24 | 16:10 | 49.873
2019-11-24 | 16:10 | 49.873
2019-11-24 | 16:10 | 49.873
2019-11-24 | 16:10 | 49.872
2019-11-24 | 16:10 | 49.872
2019-11-24 | 16:10 | 49.873
2019-11-24 | 16:10 | 49.871
2019-11-24 | 16:10 | 49.869
2019-11-24 | 16:10 | 49.867
2019-11-24 | 16:10 | 49.869
2019-11-24 | 16:10 | 49.87
2019-11-24 | 16:10 | 49.871
2019-11-24 | 16:10 | 49.872
2019-11-24 | 16:10 | 49.872
2019-11-24 | 16:10 | 49.871
2019-11-24 | 16:10 | 49.871
2019-11-24 | 16:10 | 49.87
2019-11-24 | 16:11 | 49.868
2019-11-24 | 16:11 | 49.868
2019-11-24 | 16:11 | 49.866
2019-11-24 | 16:11 | 49.866
2019-11-24 | 16:11 | 49.867
2019-11-24 | 16:11 | 49.869
2019-11-24 | 16:11 | 49.87
2019-11-24 | 16:11 | 49.872
2019-11-24 | 16:11 | 49.873
2019-11-24 | 16:11 | 49.875
2019-11-24 | 16:11 | 49.876
2019-11-24 | 16:11 | 49.875
2019-11-24 | 16:11 | 49.874
2019-11-24 | 16:11 | 49.875
2019-11-24 | 16:11 | 49.873
2019-11-24 | 16:11 | 49.873
2019-11-24 | 16:11 | 49.876
2019-11-24 | 16:11 | 49.876
2019-11-24 | 16:11 | 49.877
2019-11-24 | 16:11 | 49.879
2019-11-24 | 16:11 | 49.879
2019-11-24 | 16:11 | 49.878
2019-11-24 | 16:11 | 49.88
2019-11-24 | 16:11 | 49.879
2019-11-24 | 16:11 | 49.88
2019-11-24 | 16:11 | 49.878
2019-11-24 | 16:11 | 49.877
2019-11-24 | 16:11 | 49.875
2019-11-24 | 16:11 | 49.873
2019-11-24 | 16:11 | 49.871
2019-11-24 | 16:11 | 49.871
2019-11-24 | 16:11 | 49.872
2019-11-24 | 16:11 | 49.871
2019-11-24 | 16:11 | 49.87
2019-11-24 | 16:11 | 49.87
2019-11-24 | 16:11 | 49.868
2019-11-24 | 16:11 | 49.866
2019-11-24 | 16:11 | 49.865
2019-11-24 | 16:11 | 49.862
2019-11-24 | 16:11 | 49.859
2019-11-24 | 16:11 | 49.859
2019-11-24 | 16:11 | 49.857
2019-11-24 | 16:11 | 49.858
2019-11-24 | 16:11 | 49.859
2019-11-24 | 16:11 | 49.862
2019-11-24 | 16:11 | 49.865
2019-11-24 | 16:11 | 49.869
2019-11-24 | 16:11 | 49.873
2019-11-24 | 16:11 | 49.876
2019-11-24 | 16:11 | 49.879
2019-11-24 | 16:11 | 49.882
2019-11-24 | 16:11 | 49.884
2019-11-24 | 16:11 | 49.885
2019-11-24 | 16:11 | 49.887
2019-11-24 | 16:11 | 49.886
2019-11-24 | 16:11 | 49.887
2019-11-24 | 16:11 | 49.884
2019-11-24 | 16:11 | 49.886
2019-11-24 | 16:11 | 49.886
2019-11-24 | 16:12 | 49.887
2019-11-24 | 16:12 | 49.889
2019-11-24 | 16:12 | 49.888
2019-11-24 | 16:12 | 49.886
2019-11-24 | 16:12 | 49.884
2019-11-24 | 16:12 | 49.884
2019-11-24 | 16:12 | 49.882
2019-11-24 | 16:12 | 49.88
2019-11-24 | 16:12 | 49.881
2019-11-24 | 16:12 | 49.88
2019-11-24 | 16:12 | 49.881
2019-11-24 | 16:12 | 49.881
2019-11-24 | 16:12 | 49.882
2019-11-24 | 16:12 | 49.884
2019-11-24 | 16:12 | 49.884
2019-11-24 | 16:12 | 49.884
2019-11-24 | 16:12 | 49.886
2019-11-24 | 16:12 | 49.883
2019-11-24 | 16:12 | 49.884
2019-11-24 | 16:12 | 49.883
2019-11-24 | 16:12 | 49.882
2019-11-24 | 16:12 | 49.88
2019-11-24 | 16:12 | 49.879
2019-11-24 | 16:12 | 49.878
2019-11-24 | 16:12 | 49.877
2019-11-24 | 16:12 | 49.876
2019-11-24 | 16:12 | 49.876
2019-11-24 | 16:12 | 49.876
2019-11-24 | 16:12 | 49.877
2019-11-24 | 16:12 | 49.877
2019-11-24 | 16:12 | 49.878
2019-11-24 | 16:12 | 49.876
2019-11-24 | 16:12 | 49.876
2019-11-24 | 16:12 | 49.876
2019-11-24 | 16:12 | 49.876
2019-11-24 | 16:12 | 49.874
2019-11-24 | 16:12 | 49.873
2019-11-24 | 16:12 | 49.873
2019-11-24 | 16:12 | 49.871
2019-11-24 | 16:12 | 49.87
2019-11-24 | 16:12 | 49.868
2019-11-24 | 16:12 | 49.867
2019-11-24 | 16:12 | 49.865
2019-11-24 | 16:12 | 49.861
2019-11-24 | 16:12 | 49.859
2019-11-24 | 16:12 | 49.858
2019-11-24 | 16:12 | 49.858
2019-11-24 | 16:12 | 49.858
2019-11-24 | 16:12 | 49.86
2019-11-24 | 16:12 | 49.862
2019-11-24 | 16:12 | 49.862
2019-11-24 | 16:12 | 49.862
2019-11-24 | 16:12 | 49.86
2019-11-24 | 16:12 | 49.859
2019-11-24 | 16:12 | 49.857
2019-11-24 | 16:12 | 49.854
2019-11-24 | 16:12 | 49.853
2019-11-24 | 16:12 | 49.851
2019-11-24 | 16:12 | 49.852
2019-11-24 | 16:12 | 49.851
2019-11-24 | 16:12 | 49.854
2019-11-24 | 16:13 | 49.855
2019-11-24 | 16:13 | 49.856
2019-11-24 | 16:13 | 49.857
2019-11-24 | 16:13 | 49.856
2019-11-24 | 16:13 | 49.858
2019-11-24 | 16:13 | 49.86
2019-11-24 | 16:13 | 49.862
2019-11-24 | 16:13 | 49.864
2019-11-24 | 16:13 | 49.867
2019-11-24 | 16:13 | 49.87
2019-11-24 | 16:13 | 49.873
2019-11-24 | 16:13 | 49.875
2019-11-24 | 16:13 | 49.878
2019-11-24 | 16:13 | 49.878
2019-11-24 | 16:13 | 49.879
2019-11-24 | 16:13 | 49.879
2019-11-24 | 16:13 | 49.88
2019-11-24 | 16:13 | 49.88
2019-11-24 | 16:13 | 49.88
2019-11-24 | 16:13 | 49.879
2019-11-24 | 16:13 | 49.881
2019-11-24 | 16:13 | 49.882
2019-11-24 | 16:13 | 49.882
2019-11-24 | 16:13 | 49.881
2019-11-24 | 16:13 | 49.884
2019-11-24 | 16:13 | 49.883
2019-11-24 | 16:13 | 49.887
2019-11-24 | 16:13 | 49.889
2019-11-24 | 16:13 | 49.891
2019-11-24 | 16:13 | 49.891
2019-11-24 | 16:13 | 49.89
2019-11-24 | 16:13 | 49.891
2019-11-24 | 16:13 | 49.89
2019-11-24 | 16:13 | 49.887
2019-11-24 | 16:13 | 49.883
2019-11-24 | 16:13 | 49.884
2019-11-24 | 16:13 | 49.883
2019-11-24 | 16:13 | 49.881
2019-11-24 | 16:13 | 49.879
2019-11-24 | 16:13 | 49.878
2019-11-24 | 16:13 | 49.878
2019-11-24 | 16:13 | 49.877
2019-11-24 | 16:13 | 49.877
2019-11-24 | 16:13 | 49.876
2019-11-24 | 16:13 | 49.875
2019-11-24 | 16:13 | 49.874
2019-11-24 | 16:13 | 49.875
2019-11-24 | 16:13 | 49.876
2019-11-24 | 16:13 | 49.877
2019-11-24 | 16:13 | 49.878
2019-11-24 | 16:13 | 49.882
2019-11-24 | 16:13 | 49.884
2019-11-24 | 16:13 | 49.887
2019-11-24 | 16:13 | 49.89
2019-11-24 | 16:13 | 49.892
2019-11-24 | 16:13 | 49.895
2019-11-24 | 16:13 | 49.897
2019-11-24 | 16:13 | 49.899
2019-11-24 | 16:13 | 49.902
2019-11-24 | 16:14 | 49.902
2019-11-24 | 16:14 | 49.905
2019-11-24 | 16:14 | 49.904
2019-11-24 | 16:14 | 49.904
2019-11-24 | 16:14 | 49.905
2019-11-24 | 16:14 | 49.904
2019-11-24 | 16:14 | 49.904
2019-11-24 | 16:14 | 49.906
2019-11-24 | 16:14 | 49.907
2019-11-24 | 16:14 | 49.907
2019-11-24 | 16:14 | 49.908
2019-11-24 | 16:14 | 49.909
2019-11-24 | 16:14 | 49.912
2019-11-24 | 16:14 | 49.914
2019-11-24 | 16:14 | 49.916
2019-11-24 | 16:14 | 49.917
2019-11-24 | 16:14 | 49.92
2019-11-24 | 16:14 | 49.922
2019-11-24 | 16:14 | 49.925
2019-11-24 | 16:14 | 49.927
2019-11-24 | 16:14 | 49.93
2019-11-24 | 16:14 | 49.932
2019-11-24 | 16:14 | 49.932
2019-11-24 | 16:14 | 49.932
2019-11-24 | 16:14 | 49.931
2019-11-24 | 16:14 | 49.93
2019-11-24 | 16:14 | 49.927
2019-11-24 | 16:14 | 49.926
2019-11-24 | 16:14 | 49.925
2019-11-24 | 16:14 | 49.923
2019-11-24 | 16:14 | 49.922
2019-11-24 | 16:14 | 49.92
2019-11-24 | 16:14 | 49.918
2019-11-24 | 16:14 | 49.916
2019-11-24 | 16:14 | 49.91
2019-11-24 | 16:14 | 49.909
2019-11-24 | 16:14 | 49.907
2019-11-24 | 16:14 | 49.903
2019-11-24 | 16:14 | 49.902
2019-11-24 | 16:14 | 49.9
2019-11-24 | 16:14 | 49.899
2019-11-24 | 16:14 | 49.9
2019-11-24 | 16:14 | 49.898
2019-11-24 | 16:14 | 49.899
2019-11-24 | 16:14 | 49.898
2019-11-24 | 16:14 | 49.899
2019-11-24 | 16:14 | 49.899
2019-11-24 | 16:14 | 49.899
2019-11-24 | 16:14 | 49.899
2019-11-24 | 16:14 | 49.901
2019-11-24 | 16:14 | 49.901
2019-11-24 | 16:14 | 49.903
2019-11-24 | 16:14 | 49.902
2019-11-24 | 16:14 | 49.904
2019-11-24 | 16:14 | 49.905
2019-11-24 | 16:14 | 49.907
2019-11-24 | 16:14 | 49.909
2019-11-24 | 16:14 | 49.909
2019-11-24 | 16:14 | 49.91
2019-11-24 | 16:14 | 49.91
2019-11-24 | 16:14 | 49.909
2019-11-24 | 16:15 | 49.909
2019-11-24 | 16:15 | 49.907
2019-11-24 | 16:15 | 49.907
2019-11-24 | 16:15 | 49.907
2019-11-24 | 16:15 | 49.906
2019-11-24 | 16:15 | 49.906
2019-11-24 | 16:15 | 49.905
2019-11-24 | 16:15 | 49.905
2019-11-24 | 16:15 | 49.904
2019-11-24 | 16:15 | 49.903
2019-11-24 | 16:15 | 49.902
2019-11-24 | 16:15 | 49.901
2019-11-24 | 16:15 | 49.899
2019-11-24 | 16:15 | 49.9
2019-11-24 | 16:15 | 49.901
2019-11-24 | 16:15 | 49.902
2019-11-24 | 16:15 | 49.902
2019-11-24 | 16:15 | 49.903
2019-11-24 | 16:15 | 49.903
2019-11-24 | 16:15 | 49.903
2019-11-24 | 16:15 | 49.903
2019-11-24 | 16:15 | 49.903
2019-11-24 | 16:15 | 49.903
2019-11-24 | 16:15 | 49.902
2019-11-24 | 16:15 | 49.9
2019-11-24 | 16:15 | 49.898
2019-11-24 | 16:15 | 49.897
2019-11-24 | 16:15 | 49.896
2019-11-24 | 16:15 | 49.894
2019-11-24 | 16:15 | 49.894
2019-11-24 | 16:15 | 49.893
2019-11-24 | 16:15 | 49.894
2019-11-24 | 16:15 | 49.895
2019-11-24 | 16:15 | 49.894
2019-11-24 | 16:15 | 49.895
2019-11-24 | 16:15 | 49.895
2019-11-24 | 16:15 | 49.896
2019-11-24 | 16:15 | 49.898
2019-11-24 | 16:15 | 49.899
2019-11-24 | 16:15 | 49.902
2019-11-24 | 16:15 | 49.903
2019-11-24 | 16:15 | 49.906
2019-11-24 | 16:15 | 49.908
2019-11-24 | 16:15 | 49.91
2019-11-24 | 16:15 | 49.91
2019-11-24 | 16:15 | 49.911
2019-11-24 | 16:15 | 49.911
2019-11-24 | 16:15 | 49.91
2019-11-24 | 16:15 | 49.91
2019-11-24 | 16:15 | 49.909
2019-11-24 | 16:15 | 49.908
2019-11-24 | 16:15 | 49.907
2019-11-24 | 16:15 | 49.904
2019-11-24 | 16:15 | 49.901
2019-11-24 | 16:15 | 49.897
2019-11-24 | 16:15 | 49.894
2019-11-24 | 16:15 | 49.89
2019-11-24 | 16:15 | 49.889
2019-11-24 | 16:15 | 49.888
2019-11-24 | 16:16 | 49.888
2019-11-24 | 16:16 | 49.887
2019-11-24 | 16:16 | 49.886
2019-11-24 | 16:16 | 49.885
2019-11-24 | 16:16 | 49.883
2019-11-24 | 16:16 | 49.88
2019-11-24 | 16:16 | 49.878
2019-11-24 | 16:16 | 49.874
2019-11-24 | 16:16 | 49.87
2019-11-24 | 16:16 | 49.867
2019-11-24 | 16:16 | 49.867
2019-11-24 | 16:16 | 49.866
2019-11-24 | 16:16 | 49.865
2019-11-24 | 16:16 | 49.861
2019-11-24 | 16:16 | 49.859
2019-11-24 | 16:16 | 49.858
2019-11-24 | 16:16 | 49.857
2019-11-24 | 16:16 | 49.857
2019-11-24 | 16:16 | 49.857
2019-11-24 | 16:16 | 49.855
2019-11-24 | 16:16 | 49.853
2019-11-24 | 16:16 | 49.85
2019-11-24 | 16:16 | 49.848
2019-11-24 | 16:16 | 49.846
2019-11-24 | 16:16 | 49.845
2019-11-24 | 16:16 | 49.846
2019-11-24 | 16:16 | 49.848
2019-11-24 | 16:16 | 49.849
2019-11-24 | 16:16 | 49.85
2019-11-24 | 16:16 | 49.851
2019-11-24 | 16:16 | 49.855
2019-11-24 | 16:16 | 49.857
2019-11-24 | 16:16 | 49.859
2019-11-24 | 16:16 | 49.862
2019-11-24 | 16:16 | 49.865
2019-11-24 | 16:16 | 49.868
2019-11-24 | 16:16 | 49.87
2019-11-24 | 16:16 | 49.872
2019-11-24 | 16:16 | 49.874
2019-11-24 | 16:16 | 49.877
2019-11-24 | 16:16 | 49.881
2019-11-24 | 16:16 | 49.885
2019-11-24 | 16:16 | 49.891
2019-11-24 | 16:16 | 49.896
2019-11-24 | 16:16 | 49.902
2019-11-24 | 16:16 | 49.909
2019-11-24 | 16:16 | 49.915
2019-11-24 | 16:16 | 49.92
2019-11-24 | 16:16 | 49.927
2019-11-24 | 16:16 | 49.931
2019-11-24 | 16:16 | 49.939
2019-11-24 | 16:16 | 49.944
2019-11-24 | 16:16 | 49.948
2019-11-24 | 16:16 | 49.952
2019-11-24 | 16:16 | 49.955
2019-11-24 | 16:16 | 49.961
2019-11-24 | 16:16 | 49.966
2019-11-24 | 16:16 | 49.973
2019-11-24 | 16:16 | 49.978
2019-11-24 | 16:16 | 49.984
2019-11-24 | 16:16 | 49.986
2019-11-24 | 16:17 | 49.989
2019-11-24 | 16:17 | 49.993
2019-11-24 | 16:17 | 49.994
2019-11-24 | 16:17 | 49.996
2019-11-24 | 16:17 | 49.996
2019-11-24 | 16:17 | 49.996
2019-11-24 | 16:17 | 49.997
2019-11-24 | 16:17 | 49.999
2019-11-24 | 16:17 | 49.999
2019-11-24 | 16:17 | 50.001
2019-11-24 | 16:17 | 50.001
2019-11-24 | 16:17 | 50.002
2019-11-24 | 16:17 | 50.002
2019-11-24 | 16:17 | 50.003
2019-11-24 | 16:17 | 50.002
2019-11-24 | 16:17 | 50.002
2019-11-24 | 16:17 | 50
2019-11-24 | 16:17 | 50.001
2019-11-24 | 16:17 | 50.001
2019-11-24 | 16:17 | 50.001
2019-11-24 | 16:17 | 50
2019-11-24 | 16:17 | 50.001
2019-11-24 | 16:17 | 50.001
2019-11-24 | 16:17 | 50
2019-11-24 | 16:17 | 50
2019-11-24 | 16:17 | 49.999
2019-11-24 | 16:17 | 49.999
2019-11-24 | 16:17 | 49.998
2019-11-24 | 16:17 | 49.996
2019-11-24 | 16:17 | 49.994
2019-11-24 | 16:17 | 49.994
2019-11-24 | 16:17 | 49.992
2019-11-24 | 16:17 | 49.993
2019-11-24 | 16:17 | 49.992
2019-11-24 | 16:17 | 49.993
2019-11-24 | 16:17 | 49.992
2019-11-24 | 16:17 | 49.993
2019-11-24 | 16:17 | 49.995
2019-11-24 | 16:17 | 49.995
2019-11-24 | 16:17 | 49.996
2019-11-24 | 16:17 | 49.995
2019-11-24 | 16:17 | 49.995
2019-11-24 | 16:17 | 49.994
2019-11-24 | 16:17 | 49.993
2019-11-24 | 16:17 | 49.993
2019-11-24 | 16:17 | 49.994
2019-11-24 | 16:17 | 49.995
2019-11-24 | 16:17 | 49.995
2019-11-24 | 16:17 | 49.997
2019-11-24 | 16:17 | 49.999
2019-11-24 | 16:17 | 50.001
2019-11-24 | 16:17 | 50.003
2019-11-24 | 16:17 | 50.005
2019-11-24 | 16:17 | 50.007
2019-11-24 | 16:17 | 50.008
2019-11-24 | 16:17 | 50.008
2019-11-24 | 16:17 | 50.009
2019-11-24 | 16:17 | 50.008
2019-11-24 | 16:17 | 50.007
2019-11-24 | 16:18 | 50.009
2019-11-24 | 16:18 | 50.011
2019-11-24 | 16:18 | 50.012
2019-11-24 | 16:18 | 50.012
2019-11-24 | 16:18 | 50.012
2019-11-24 | 16:18 | 50.01
2019-11-24 | 16:18 | 50.011
2019-11-24 | 16:18 | 50.009
2019-11-24 | 16:18 | 50.007
2019-11-24 | 16:18 | 50.005
2019-11-24 | 16:18 | 50.002
2019-11-24 | 16:18 | 50.002
2019-11-24 | 16:18 | 49.998
2019-11-24 | 16:18 | 49.997
2019-11-24 | 16:18 | 49.994
2019-11-24 | 16:18 | 49.994
2019-11-24 | 16:18 | 49.993
2019-11-24 | 16:18 | 49.993
2019-11-24 | 16:18 | 49.993
2019-11-24 | 16:18 | 49.994
2019-11-24 | 16:18 | 49.993
2019-11-24 | 16:18 | 49.994
2019-11-24 | 16:18 | 49.994
2019-11-24 | 16:18 | 49.996
2019-11-24 | 16:18 | 49.996
2019-11-24 | 16:18 | 49.996
2019-11-24 | 16:18 | 49.996
2019-11-24 | 16:18 | 49.997
2019-11-24 | 16:18 | 49.995
2019-11-24 | 16:18 | 49.995

## Event 20191130-1
In UTC
Date | Time | Freq
2019-11-30 | 22:19 | 49.942
2019-11-30 | 22:19 | 49.941
2019-11-30 | 22:19 | 49.941
2019-11-30 | 22:19 | 49.94
2019-11-30 | 22:19 | 49.94
2019-11-30 | 22:19 | 49.938
2019-11-30 | 22:19 | 49.935
2019-11-30 | 22:19 | 49.931
2019-11-30 | 22:19 | 49.93
2019-11-30 | 22:19 | 49.931
2019-11-30 | 22:19 | 49.933
2019-11-30 | 22:19 | 49.933
2019-11-30 | 22:19 | 49.934
2019-11-30 | 22:19 | 49.934
2019-11-30 | 22:19 | 49.932
2019-11-30 | 22:19 | 49.932
2019-11-30 | 22:19 | 49.929
2019-11-30 | 22:19 | 49.926
2019-11-30 | 22:19 | 49.924
2019-11-30 | 22:19 | 49.924
2019-11-30 | 22:19 | 49.926
2019-11-30 | 22:19 | 49.928
2019-11-30 | 22:19 | 49.93
2019-11-30 | 22:19 | 49.931
2019-11-30 | 22:19 | 49.933
2019-11-30 | 22:19 | 49.934
2019-11-30 | 22:19 | 49.936
2019-11-30 | 22:19 | 49.937
2019-11-30 | 22:19 | 49.938
2019-11-30 | 22:19 | 49.937
2019-11-30 | 22:20 | 49.936
2019-11-30 | 22:20 | 49.937
2019-11-30 | 22:20 | 49.937
2019-11-30 | 22:20 | 49.937
2019-11-30 | 22:20 | 49.94
2019-11-30 | 22:20 | 49.942
2019-11-30 | 22:20 | 49.943
2019-11-30 | 22:20 | 49.945
2019-11-30 | 22:20 | 49.947
2019-11-30 | 22:20 | 49.949
2019-11-30 | 22:20 | 49.949
2019-11-30 | 22:20 | 49.948
2019-11-30 | 22:20 | 49.946
2019-11-30 | 22:20 | 49.944
2019-11-30 | 22:20 | 49.942
2019-11-30 | 22:20 | 49.943
2019-11-30 | 22:20 | 49.943
2019-11-30 | 22:20 | 49.943
2019-11-30 | 22:20 | 49.943
2019-11-30 | 22:20 | 49.942
2019-11-30 | 22:20 | 49.942
2019-11-30 | 22:20 | 49.941
2019-11-30 | 22:20 | 49.94
2019-11-30 | 22:20 | 49.94
2019-11-30 | 22:20 | 49.94
2019-11-30 | 22:20 | 49.939
2019-11-30 | 22:20 | 49.94
2019-11-30 | 22:20 | 49.941
2019-11-30 | 22:20 | 49.942
2019-11-30 | 22:20 | 49.942
2019-11-30 | 22:20 | 49.941
2019-11-30 | 22:20 | 49.939
2019-11-30 | 22:20 | 49.938
2019-11-30 | 22:20 | 49.936
2019-11-30 | 22:20 | 49.934
2019-11-30 | 22:20 | 49.932
2019-11-30 | 22:20 | 49.929
2019-11-30 | 22:20 | 49.928
2019-11-30 | 22:20 | 49.927
2019-11-30 | 22:20 | 49.927
2019-11-30 | 22:20 | 49.925
2019-11-30 | 22:20 | 49.923
2019-11-30 | 22:20 | 49.921
2019-11-30 | 22:20 | 49.919
2019-11-30 | 22:20 | 49.916
2019-11-30 | 22:20 | 49.913
2019-11-30 | 22:20 | 49.912
2019-11-30 | 22:20 | 49.912
2019-11-30 | 22:20 | 49.911
2019-11-30 | 22:20 | 49.912
2019-11-30 | 22:20 | 49.911
2019-11-30 | 22:20 | 49.913
2019-11-30 | 22:20 | 49.915
2019-11-30 | 22:20 | 49.916
2019-11-30 | 22:20 | 49.919
2019-11-30 | 22:20 | 49.919
2019-11-30 | 22:20 | 49.919
2019-11-30 | 22:20 | 49.92
2019-11-30 | 22:20 | 49.92
2019-11-30 | 22:20 | 49.923
2019-11-30 | 22:20 | 49.924
2019-11-30 | 22:21 | 49.926
2019-11-30 | 22:21 | 49.925
2019-11-30 | 22:21 | 49.922
2019-11-30 | 22:21 | 49.919
2019-11-30 | 22:21 | 49.914
2019-11-30 | 22:21 | 49.912
2019-11-30 | 22:21 | 49.906
2019-11-30 | 22:21 | 49.896
2019-11-30 | 22:21 | 49.89
2019-11-30 | 22:21 | 49.885
2019-11-30 | 22:21 | 49.882
2019-11-30 | 22:21 | 49.88
2019-11-30 | 22:21 | 49.88
2019-11-30 | 22:21 | 49.88
2019-11-30 | 22:21 | 49.882
2019-11-30 | 22:21 | 49.884
2019-11-30 | 22:21 | 49.884
2019-11-30 | 22:21 | 49.885
2019-11-30 | 22:21 | 49.885
2019-11-30 | 22:21 | 49.885
2019-11-30 | 22:21 | 49.885
2019-11-30 | 22:21 | 49.883
2019-11-30 | 22:21 | 49.884
2019-11-30 | 22:21 | 49.883
2019-11-30 | 22:21 | 49.883
2019-11-30 | 22:21 | 49.881
2019-11-30 | 22:21 | 49.883
2019-11-30 | 22:21 | 49.883
2019-11-30 | 22:21 | 49.882
2019-11-30 | 22:21 | 49.883
2019-11-30 | 22:21 | 49.882
2019-11-30 | 22:21 | 49.857
2019-11-30 | 22:21 | 49.836
2019-11-30 | 22:21 | 49.824
2019-11-30 | 22:21 | 49.815
2019-11-30 | 22:21 | 49.809
2019-11-30 | 22:21 | 49.806
2019-11-30 | 22:21 | 49.804
2019-11-30 | 22:21 | 49.806
2019-11-30 | 22:21 | 49.808
2019-11-30 | 22:21 | 49.81
2019-11-30 | 22:21 | 49.814
2019-11-30 | 22:21 | 49.817
2019-11-30 | 22:21 | 49.82
2019-11-30 | 22:21 | 49.823
2019-11-30 | 22:21 | 49.826
2019-11-30 | 22:21 | 49.827
2019-11-30 | 22:21 | 49.827
2019-11-30 | 22:21 | 49.826
2019-11-30 | 22:21 | 49.825
2019-11-30 | 22:21 | 49.825
2019-11-30 | 22:21 | 49.827
2019-11-30 | 22:21 | 49.826
2019-11-30 | 22:21 | 49.827
2019-11-30 | 22:21 | 49.827
2019-11-30 | 22:21 | 49.827
2019-11-30 | 22:21 | 49.828
2019-11-30 | 22:21 | 49.829
2019-11-30 | 22:21 | 49.829
2019-11-30 | 22:22 | 49.831
2019-11-30 | 22:22 | 49.831
2019-11-30 | 22:22 | 49.833
2019-11-30 | 22:22 | 49.835
2019-11-30 | 22:22 | 49.836
2019-11-30 | 22:22 | 49.838
2019-11-30 | 22:22 | 49.838
2019-11-30 | 22:22 | 49.838
2019-11-30 | 22:22 | 49.837
2019-11-30 | 22:22 | 49.837
2019-11-30 | 22:22 | 49.835
2019-11-30 | 22:22 | 49.834
2019-11-30 | 22:22 | 49.832
2019-11-30 | 22:22 | 49.831
2019-11-30 | 22:22 | 49.829
2019-11-30 | 22:22 | 49.828
2019-11-30 | 22:22 | 49.83
2019-11-30 | 22:22 | 49.831
2019-11-30 | 22:22 | 49.831
2019-11-30 | 22:22 | 49.832
2019-11-30 | 22:22 | 49.833
2019-11-30 | 22:22 | 49.832
2019-11-30 | 22:22 | 49.832
2019-11-30 | 22:22 | 49.833
2019-11-30 | 22:22 | 49.835
2019-11-30 | 22:22 | 49.836
2019-11-30 | 22:22 | 49.837
2019-11-30 | 22:22 | 49.838
2019-11-30 | 22:22 | 49.837
2019-11-30 | 22:22 | 49.836
2019-11-30 | 22:22 | 49.835
2019-11-30 | 22:22 | 49.836
2019-11-30 | 22:22 | 49.837
2019-11-30 | 22:22 | 49.838
2019-11-30 | 22:22 | 49.84
2019-11-30 | 22:22 | 49.839
2019-11-30 | 22:22 | 49.839
2019-11-30 | 22:22 | 49.84
2019-11-30 | 22:22 | 49.839
2019-11-30 | 22:22 | 49.836
2019-11-30 | 22:22 | 49.835
2019-11-30 | 22:22 | 49.835
2019-11-30 | 22:22 | 49.833
2019-11-30 | 22:22 | 49.833
2019-11-30 | 22:22 | 49.832
2019-11-30 | 22:22 | 49.83
2019-11-30 | 22:22 | 49.827
2019-11-30 | 22:22 | 49.828
2019-11-30 | 22:22 | 49.827
2019-11-30 | 22:22 | 49.829
2019-11-30 | 22:22 | 49.832
2019-11-30 | 22:22 | 49.835
2019-11-30 | 22:22 | 49.838
2019-11-30 | 22:22 | 49.842
2019-11-30 | 22:22 | 49.848
2019-11-30 | 22:22 | 49.853
2019-11-30 | 22:22 | 49.86
2019-11-30 | 22:22 | 49.87
2019-11-30 | 22:22 | 49.877
2019-11-30 | 22:22 | 49.882
2019-11-30 | 22:22 | 49.889
2019-11-30 | 22:23 | 49.893
2019-11-30 | 22:23 | 49.897
2019-11-30 | 22:23 | 49.901
2019-11-30 | 22:23 | 49.904
2019-11-30 | 22:23 | 49.907
2019-11-30 | 22:23 | 49.91
2019-11-30 | 22:23 | 49.91
2019-11-30 | 22:23 | 49.909
2019-11-30 | 22:23 | 49.91
2019-11-30 | 22:23 | 49.908
2019-11-30 | 22:23 | 49.905
2019-11-30 | 22:23 | 49.904
2019-11-30 | 22:23 | 49.902
2019-11-30 | 22:23 | 49.9
2019-11-30 | 22:23 | 49.899
2019-11-30 | 22:23 | 49.899
2019-11-30 | 22:23 | 49.901
2019-11-30 | 22:23 | 49.9
2019-11-30 | 22:23 | 49.901
2019-11-30 | 22:23 | 49.904
2019-11-30 | 22:23 | 49.905
2019-11-30 | 22:23 | 49.906
2019-11-30 | 22:23 | 49.909
2019-11-30 | 22:23 | 49.908
2019-11-30 | 22:23 | 49.904
2019-11-30 | 22:23 | 49.902
2019-11-30 | 22:23 | 49.9
2019-11-30 | 22:23 | 49.901
2019-11-30 | 22:23 | 49.903
2019-11-30 | 22:23 | 49.904
2019-11-30 | 22:23 | 49.905
2019-11-30 | 22:23 | 49.904
2019-11-30 | 22:23 | 49.902
2019-11-30 | 22:23 | 49.9
2019-11-30 | 22:23 | 49.898
2019-11-30 | 22:23 | 49.894
2019-11-30 | 22:23 | 49.891
2019-11-30 | 22:23 | 49.89
2019-11-30 | 22:23 | 49.89
2019-11-30 | 22:23 | 49.891
2019-11-30 | 22:23 | 49.892
2019-11-30 | 22:23 | 49.889
2019-11-30 | 22:23 | 49.889
2019-11-30 | 22:23 | 49.891
2019-11-30 | 22:23 | 49.89
2019-11-30 | 22:23 | 49.89
2019-11-30 | 22:23 | 49.89
2019-11-30 | 22:23 | 49.889
2019-11-30 | 22:23 | 49.888
2019-11-30 | 22:23 | 49.89
2019-11-30 | 22:23 | 49.89
2019-11-30 | 22:23 | 49.892
2019-11-30 | 22:23 | 49.896
2019-11-30 | 22:23 | 49.898
2019-11-30 | 22:23 | 49.898
2019-11-30 | 22:23 | 49.899
2019-11-30 | 22:23 | 49.901
2019-11-30 | 22:23 | 49.902
2019-11-30 | 22:23 | 49.902
2019-11-30 | 22:24 | 49.902
2019-11-30 | 22:24 | 49.901
2019-11-30 | 22:24 | 49.9
2019-11-30 | 22:24 | 49.9
2019-11-30 | 22:24 | 49.899
2019-11-30 | 22:24 | 49.898
2019-11-30 | 22:24 | 49.898
2019-11-30 | 22:24 | 49.898
2019-11-30 | 22:24 | 49.899
2019-11-30 | 22:24 | 49.899
2019-11-30 | 22:24 | 49.899
2019-11-30 | 22:24 | 49.901
2019-11-30 | 22:24 | 49.903
2019-11-30 | 22:24 | 49.903
2019-11-30 | 22:24 | 49.905
2019-11-30 | 22:24 | 49.907
2019-11-30 | 22:24 | 49.909
2019-11-30 | 22:24 | 49.911
2019-11-30 | 22:24 | 49.913
2019-11-30 | 22:24 | 49.914
2019-11-30 | 22:24 | 49.914
2019-11-30 | 22:24 | 49.916
2019-11-30 | 22:24 | 49.918
2019-11-30 | 22:24 | 49.917
2019-11-30 | 22:24 | 49.918
2019-11-30 | 22:24 | 49.917
2019-11-30 | 22:24 | 49.915
2019-11-30 | 22:24 | 49.913
2019-11-30 | 22:24 | 49.912
2019-11-30 | 22:24 | 49.91
2019-11-30 | 22:24 | 49.906
2019-11-30 | 22:24 | 49.905
2019-11-30 | 22:24 | 49.904
2019-11-30 | 22:24 | 49.902
2019-11-30 | 22:24 | 49.902
2019-11-30 | 22:24 | 49.901
2019-11-30 | 22:24 | 49.901
2019-11-30 | 22:24 | 49.899
2019-11-30 | 22:24 | 49.898
2019-11-30 | 22:24 | 49.896
2019-11-30 | 22:24 | 49.893
2019-11-30 | 22:24 | 49.891
2019-11-30 | 22:24 | 49.891
2019-11-30 | 22:24 | 49.892
2019-11-30 | 22:24 | 49.894
2019-11-30 | 22:24 | 49.896
2019-11-30 | 22:24 | 49.897
2019-11-30 | 22:24 | 49.898
2019-11-30 | 22:24 | 49.899
2019-11-30 | 22:24 | 49.902
2019-11-30 | 22:24 | 49.903
2019-11-30 | 22:24 | 49.904
2019-11-30 | 22:24 | 49.907
2019-11-30 | 22:24 | 49.908
2019-11-30 | 22:24 | 49.91
2019-11-30 | 22:24 | 49.91
2019-11-30 | 22:24 | 49.909
2019-11-30 | 22:24 | 49.909
2019-11-30 | 22:24 | 49.909
2019-11-30 | 22:24 | 49.908
2019-11-30 | 22:24 | 49.91
2019-11-30 | 22:25 | 49.909
2019-11-30 | 22:25 | 49.909
2019-11-30 | 22:25 | 49.908
2019-11-30 | 22:25 | 49.909
2019-11-30 | 22:25 | 49.908
2019-11-30 | 22:25 | 49.909
2019-11-30 | 22:25 | 49.91
2019-11-30 | 22:25 | 49.911
2019-11-30 | 22:25 | 49.914
2019-11-30 | 22:25 | 49.917
2019-11-30 | 22:25 | 49.917
2019-11-30 | 22:25 | 49.918
2019-11-30 | 22:25 | 49.919
2019-11-30 | 22:25 | 49.92
2019-11-30 | 22:25 | 49.921
2019-11-30 | 22:25 | 49.922
2019-11-30 | 22:25 | 49.921
2019-11-30 | 22:25 | 49.918
2019-11-30 | 22:25 | 49.919
2019-11-30 | 22:25 | 49.918
2019-11-30 | 22:25 | 49.918
2019-11-30 | 22:25 | 49.92
2019-11-30 | 22:25 | 49.921
2019-11-30 | 22:25 | 49.923
2019-11-30 | 22:25 | 49.923
2019-11-30 | 22:25 | 49.924
2019-11-30 | 22:25 | 49.924
2019-11-30 | 22:25 | 49.925
2019-11-30 | 22:25 | 49.924
2019-11-30 | 22:25 | 49.923
2019-11-30 | 22:25 | 49.923
2019-11-30 | 22:25 | 49.921
2019-11-30 | 22:25 | 49.92
2019-11-30 | 22:25 | 49.921
2019-11-30 | 22:25 | 49.924
2019-11-30 | 22:25 | 49.925
2019-11-30 | 22:25 | 49.926
2019-11-30 | 22:25 | 49.926
2019-11-30 | 22:25 | 49.926
2019-11-30 | 22:25 | 49.925
2019-11-30 | 22:25 | 49.925
2019-11-30 | 22:25 | 49.922
2019-11-30 | 22:25 | 49.921
2019-11-30 | 22:25 | 49.923
2019-11-30 | 22:25 | 49.926
2019-11-30 | 22:25 | 49.932
2019-11-30 | 22:25 | 49.939
2019-11-30 | 22:25 | 49.942
2019-11-30 | 22:25 | 49.945
2019-11-30 | 22:25 | 49.947
2019-11-30 | 22:25 | 49.948
2019-11-30 | 22:25 | 49.946
2019-11-30 | 22:25 | 49.943
2019-11-30 | 22:25 | 49.939
2019-11-30 | 22:25 | 49.936
2019-11-30 | 22:25 | 49.933
2019-11-30 | 22:25 | 49.932
2019-11-30 | 22:25 | 49.929
2019-11-30 | 22:25 | 49.927
2019-11-30 | 22:26 | 49.927
2019-11-30 | 22:26 | 49.931
2019-11-30 | 22:26 | 49.935
2019-11-30 | 22:26 | 49.938
2019-11-30 | 22:26 | 49.94
2019-11-30 | 22:26 | 49.942
2019-11-30 | 22:26 | 49.944
2019-11-30 | 22:26 | 49.945
2019-11-30 | 22:26 | 49.946
2019-11-30 | 22:26 | 49.946
2019-11-30 | 22:26 | 49.945
2019-11-30 | 22:26 | 49.943
2019-11-30 | 22:26 | 49.942
2019-11-30 | 22:26 | 49.94
2019-11-30 | 22:26 | 49.939
2019-11-30 | 22:26 | 49.939
2019-11-30 | 22:26 | 49.939
2019-11-30 | 22:26 | 49.941
2019-11-30 | 22:26 | 49.943
2019-11-30 | 22:26 | 49.947
2019-11-30 | 22:26 | 49.95
2019-11-30 | 22:26 | 49.954
2019-11-30 | 22:26 | 49.96
2019-11-30 | 22:26 | 49.964
2019-11-30 | 22:26 | 49.967
2019-11-30 | 22:26 | 49.966
2019-11-30 | 22:26 | 49.966
2019-11-30 | 22:26 | 49.966
2019-11-30 | 22:26 | 49.965
2019-11-30 | 22:26 | 49.965
2019-11-30 | 22:26 | 49.963
2019-11-30 | 22:26 | 49.961
2019-11-30 | 22:26 | 49.959
2019-11-30 | 22:26 | 49.959
2019-11-30 | 22:26 | 49.957
2019-11-30 | 22:26 | 49.956
2019-11-30 | 22:26 | 49.954
2019-11-30 | 22:26 | 49.954
2019-11-30 | 22:26 | 49.953
2019-11-30 | 22:26 | 49.953
2019-11-30 | 22:26 | 49.952
2019-11-30 | 22:26 | 49.953
2019-11-30 | 22:26 | 49.953
2019-11-30 | 22:26 | 49.953
2019-11-30 | 22:26 | 49.952
2019-11-30 | 22:26 | 49.952
2019-11-30 | 22:26 | 49.954
2019-11-30 | 22:26 | 49.956
2019-11-30 | 22:26 | 49.955
2019-11-30 | 22:26 | 49.956
2019-11-30 | 22:26 | 49.956
2019-11-30 | 22:26 | 49.956
2019-11-30 | 22:26 | 49.955
2019-11-30 | 22:26 | 49.955
2019-11-30 | 22:26 | 49.956
2019-11-30 | 22:26 | 49.958
2019-11-30 | 22:26 | 49.96
2019-11-30 | 22:26 | 49.962
2019-11-30 | 22:26 | 49.964
2019-11-30 | 22:26 | 49.966
2019-11-30 | 22:26 | 49.966
2019-11-30 | 22:27 | 49.965
2019-11-30 | 22:27 | 49.965
2019-11-30 | 22:27 | 49.964
2019-11-30 | 22:27 | 49.966
2019-11-30 | 22:27 | 49.967
2019-11-30 | 22:27 | 49.969
2019-11-30 | 22:27 | 49.969
2019-11-30 | 22:27 | 49.971
2019-11-30 | 22:27 | 49.971
2019-11-30 | 22:27 | 49.972
2019-11-30 | 22:27 | 49.973
2019-11-30 | 22:27 | 49.974
2019-11-30 | 22:27 | 49.973
2019-11-30 | 22:27 | 49.972
2019-11-30 | 22:27 | 49.971
2019-11-30 | 22:27 | 49.971
2019-11-30 | 22:27 | 49.969
2019-11-30 | 22:27 | 49.967
2019-11-30 | 22:27 | 49.964
2019-11-30 | 22:27 | 49.961
2019-11-30 | 22:27 | 49.958
2019-11-30 | 22:27 | 49.956
2019-11-30 | 22:27 | 49.956
2019-11-30 | 22:27 | 49.956
2019-11-30 | 22:27 | 49.957
2019-11-30 | 22:27 | 49.959
2019-11-30 | 22:27 | 49.961
2019-11-30 | 22:27 | 49.963
2019-11-30 | 22:27 | 49.966
2019-11-30 | 22:27 | 49.968
2019-11-30 | 22:27 | 49.967
2019-11-30 | 22:27 | 49.964
2019-11-30 | 22:27 | 49.96
2019-11-30 | 22:27 | 49.955
2019-11-30 | 22:27 | 49.95
2019-11-30 | 22:27 | 49.949
2019-11-30 | 22:27 | 49.949
2019-11-30 | 22:27 | 49.952
2019-11-30 | 22:27 | 49.952
2019-11-30 | 22:27 | 49.954
2019-11-30 | 22:27 | 49.955
2019-11-30 | 22:27 | 49.955
2019-11-30 | 22:27 | 49.954
2019-11-30 | 22:27 | 49.953
2019-11-30 | 22:27 | 49.951
2019-11-30 | 22:27 | 49.951
2019-11-30 | 22:27 | 49.953
2019-11-30 | 22:27 | 49.959
2019-11-30 | 22:27 | 49.964
2019-11-30 | 22:27 | 49.968
2019-11-30 | 22:27 | 49.974
2019-11-30 | 22:27 | 49.977
2019-11-30 | 22:27 | 49.98
2019-11-30 | 22:27 | 49.982
2019-11-30 | 22:27 | 49.981
2019-11-30 | 22:27 | 49.98
2019-11-30 | 22:27 | 49.98
2019-11-30 | 22:27 | 49.978
2019-11-30 | 22:27 | 49.976
2019-11-30 | 22:28 | 49.975
2019-11-30 | 22:28 | 49.974
2019-11-30 | 22:28 | 49.976
2019-11-30 | 22:28 | 49.977
2019-11-30 | 22:28 | 49.977
2019-11-30 | 22:28 | 49.977
2019-11-30 | 22:28 | 49.977
2019-11-30 | 22:28 | 49.977
2019-11-30 | 22:28 | 49.977
2019-11-30 | 22:28 | 49.978
2019-11-30 | 22:28 | 49.977
2019-11-30 | 22:28 | 49.976
2019-11-30 | 22:28 | 49.977
2019-11-30 | 22:28 | 49.979
2019-11-30 | 22:28 | 49.979
2019-11-30 | 22:28 | 49.979
2019-11-30 | 22:28 | 49.98
2019-11-30 | 22:28 | 49.982
2019-11-30 | 22:28 | 49.984
2019-11-30 | 22:28 | 49.986
2019-11-30 | 22:28 | 49.988
2019-11-30 | 22:28 | 49.991
2019-11-30 | 22:28 | 49.994
2019-11-30 | 22:28 | 49.999
2019-11-30 | 22:28 | 50.005
2019-11-30 | 22:28 | 50.01
2019-11-30 | 22:28 | 50.013
2019-11-30 | 22:28 | 50.014
2019-11-30 | 22:28 | 50.016
2019-11-30 | 22:28 | 50.016