## Notes
Subject | Notes
System inertia: method of calculation | H=(f*∆P)/(2*RoCoF) H is system inertia; f is the starting frequency; ∆P is the system imbalance; RoCoF is the rate of change of frequency; Note that smaller losses will have less accurate system inertia calculations
RoCoF: method of calculation | RoCoF=(f_500ms-f_0ms)/500ms RoCoF is calculated using 500ms sliding window. RoCoF is the rate of change of frequency; f is the frequency; Note that smaller losses will have less accurate ROCOF calculations
Voltage Dip | Transient Voltage Dip with loss % and duration measured at the local substation
'Immediately before the Significant Event' | The starting frequency indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.
'Immediately after the Significant Event' | The maximum frequency deviation indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.

## Report
|  |  |  | (i) the time(s) in hh.mm.ss of the Significant Event and any potentially related occurrences; | (ii) any known or reported loss of Embedded Power Station(s) with locations and ratings where available; | (iii) the Frequency record (in table and graphical format) at <=1 second intervals for 1 minute before and 1 minute after the Significant Event; | (iv) the Frequency (to 2 decimal places) immediately before the Significant Event; | (v) the Frequency (to 2 decimal places) immediately after the Significant Event; | (vi) the maximum rate of change of Frequency recorded during the Significant Event over a specified time period of 500ms; | (vii) where known, the MW of all individual losses or trips related to the Significant Event; |  | (viii) where known, the identity of the Users and Network Operator of all demand losses or trips related to the Significant Event; | (ix) the location of any reported Transmission fault on the network diagram and geographically; | (x) the extent of any voltage dip associated with the Significant Event; | (xi) an estimate of system inertia in MWs at the time of the Significant Event along with how it has been calculated; and | (xii) any other data available that is of value to gain a clearer understanding of the Significant Event and its potential implications; and
Event Ref | Event Name | Notes | Date (Local) | Time (Local) | Loss of Embedded Power Station | Frequency Record | Pre-Event Frequency | Post-Event Frequency | RoCoF over 500ms | Individual Loss | System Imbalance | Demand loss of Users/DNOs related to event | Location of transmission fault | Voltage Dip | System Inertia | Additional data
Event Date-Number | Text | Text | DD/MM/YYYY | hh:mm:ss | MW | Text | Hz | Hz | Hz/s | Text+MW | MW | Text+MW | Text | % | GWs | Text
Event 20200302-1 | Trip of PEMB-31 |  | 2020-03-02 | 11:35 | N/A | Refer to tab 'Event 20200302-1' | 50.05 | 49.835 | -0.045 | 431 | -431 | N/A | N/A | N/A | 239.6839
Event 20200306-1 | Trip of NEMO |  | 2020-03-06 | 23:56 | N/A | Refer to tab 'Event 20200306-1' | 50.05 | 49.694 | -0.106 | 1000 | -1000 | N/A | N/A | N/A | 236.0849
Event 20200307-1 | Trip of PEHE-1 |  | 2020-03-07 | 1:06 | N/A | Refer to tab 'Event 20200307-1' | 50.007 | 49.842 | -0.04 | 600 | -600 | N/A | N/A | N/A | 375.0525
Event 20200307-2 | Trip of GRAI-8 |  | 2020-03-07 | 4:41 | N/A | Refer to tab 'Event 20200307-2' | 49.994 | 49.942 | -0.017 | 425 | -425 | N/A | N/A | N/A | 624.925
Event 20200318-1 | Trip of EECL-1 |  | 2020-03-18 | 15:11 | N/A | Refer to tab 'Event 20200318-1' | 49.943 | 49.795 | -0.043 | 373 | -373 | N/A | N/A | N/A | 216.6132
Event 20200320-1 | Loss of COSO-1 | GT tripped, output reduced from 303MW at 21:01 to 0 MW at 21:22 | 2020-03-20 | 21:01 | N/A | Refer to tab 'Event 20200320-1' | 49.846 | 49.808 | N/A | 303 | -303 | N/A | N/A | N/A | N/A

## Event 20200302-1
In UTC
Date | Time | Freq
2020-03-02 | 11:34 | 49.974
2020-03-02 | 11:34 | 49.974
2020-03-02 | 11:34 | 49.975
2020-03-02 | 11:34 | 49.975
2020-03-02 | 11:34 | 49.975
2020-03-02 | 11:34 | 49.977
2020-03-02 | 11:34 | 49.979
2020-03-02 | 11:34 | 49.982
2020-03-02 | 11:34 | 49.984
2020-03-02 | 11:34 | 49.988
2020-03-02 | 11:34 | 49.99
2020-03-02 | 11:34 | 49.993
2020-03-02 | 11:34 | 49.996
2020-03-02 | 11:34 | 49.997
2020-03-02 | 11:34 | 50
2020-03-02 | 11:34 | 50
2020-03-02 | 11:34 | 50.002
2020-03-02 | 11:34 | 50.003
2020-03-02 | 11:34 | 50.006
2020-03-02 | 11:34 | 50.011
2020-03-02 | 11:34 | 50.017
2020-03-02 | 11:34 | 50.021
2020-03-02 | 11:34 | 50.025
2020-03-02 | 11:34 | 50.027
2020-03-02 | 11:34 | 50.028
2020-03-02 | 11:34 | 50.03
2020-03-02 | 11:34 | 50.032
2020-03-02 | 11:34 | 50.034
2020-03-02 | 11:34 | 50.035
2020-03-02 | 11:34 | 50.036
2020-03-02 | 11:34 | 50.037
2020-03-02 | 11:35 | 50.038
2020-03-02 | 11:35 | 50.039
2020-03-02 | 11:35 | 50.039
2020-03-02 | 11:35 | 50.039
2020-03-02 | 11:35 | 50.037
2020-03-02 | 11:35 | 50.035
2020-03-02 | 11:35 | 50.034
2020-03-02 | 11:35 | 50.034
2020-03-02 | 11:35 | 50.031
2020-03-02 | 11:35 | 50.03
2020-03-02 | 11:35 | 50.029
2020-03-02 | 11:35 | 50.029
2020-03-02 | 11:35 | 50.026
2020-03-02 | 11:35 | 50.024
2020-03-02 | 11:35 | 50.022
2020-03-02 | 11:35 | 50.017
2020-03-02 | 11:35 | 50.013
2020-03-02 | 11:35 | 50.009
2020-03-02 | 11:35 | 50.005
2020-03-02 | 11:35 | 50.002
2020-03-02 | 11:35 | 49.997
2020-03-02 | 11:35 | 49.994
2020-03-02 | 11:35 | 49.991
2020-03-02 | 11:35 | 49.99
2020-03-02 | 11:35 | 49.988
2020-03-02 | 11:35 | 49.988
2020-03-02 | 11:35 | 49.989
2020-03-02 | 11:35 | 49.989
2020-03-02 | 11:35 | 49.989
2020-03-02 | 11:35 | 49.99
2020-03-02 | 11:35 | 49.987
2020-03-02 | 11:35 | 49.986
2020-03-02 | 11:35 | 49.984
2020-03-02 | 11:35 | 49.985
2020-03-02 | 11:35 | 49.984
2020-03-02 | 11:35 | 49.983
2020-03-02 | 11:35 | 49.983
2020-03-02 | 11:35 | 49.983
2020-03-02 | 11:35 | 49.984
2020-03-02 | 11:35 | 49.985
2020-03-02 | 11:35 | 49.985
2020-03-02 | 11:35 | 49.986
2020-03-02 | 11:35 | 49.988
2020-03-02 | 11:35 | 49.987
2020-03-02 | 11:35 | 49.986
2020-03-02 | 11:35 | 49.986
2020-03-02 | 11:35 | 49.985
2020-03-02 | 11:35 | 49.985
2020-03-02 | 11:35 | 49.986
2020-03-02 | 11:35 | 49.989
2020-03-02 | 11:35 | 49.992
2020-03-02 | 11:35 | 49.996
2020-03-02 | 11:35 | 50.001
2020-03-02 | 11:35 | 50.005
2020-03-02 | 11:35 | 50.005
2020-03-02 | 11:35 | 49.997
2020-03-02 | 11:35 | 49.989
2020-03-02 | 11:35 | 49.982
2020-03-02 | 11:35 | 49.981
2020-03-02 | 11:36 | 49.961
2020-03-02 | 11:36 | 49.937
2020-03-02 | 11:36 | 49.92
2020-03-02 | 11:36 | 49.903
2020-03-02 | 11:36 | 49.893
2020-03-02 | 11:36 | 49.884
2020-03-02 | 11:36 | 49.875
2020-03-02 | 11:36 | 49.868
2020-03-02 | 11:36 | 49.863
2020-03-02 | 11:36 | 49.859
2020-03-02 | 11:36 | 49.856
2020-03-02 | 11:36 | 49.856
2020-03-02 | 11:36 | 49.856
2020-03-02 | 11:36 | 49.856
2020-03-02 | 11:36 | 49.858
2020-03-02 | 11:36 | 49.859
2020-03-02 | 11:36 | 49.861
2020-03-02 | 11:36 | 49.864
2020-03-02 | 11:36 | 49.866
2020-03-02 | 11:36 | 49.866
2020-03-02 | 11:36 | 49.867
2020-03-02 | 11:36 | 49.868
2020-03-02 | 11:36 | 49.868
2020-03-02 | 11:36 | 49.867
2020-03-02 | 11:36 | 49.869
2020-03-02 | 11:36 | 49.87
2020-03-02 | 11:36 | 49.873
2020-03-02 | 11:36 | 49.873
2020-03-02 | 11:36 | 49.874
2020-03-02 | 11:36 | 49.873
2020-03-02 | 11:36 | 49.871
2020-03-02 | 11:36 | 49.871
2020-03-02 | 11:36 | 49.87
2020-03-02 | 11:36 | 49.87
2020-03-02 | 11:36 | 49.869
2020-03-02 | 11:36 | 49.866
2020-03-02 | 11:36 | 49.866
2020-03-02 | 11:36 | 49.864
2020-03-02 | 11:36 | 49.863
2020-03-02 | 11:36 | 49.862
2020-03-02 | 11:36 | 49.862
2020-03-02 | 11:36 | 49.861
2020-03-02 | 11:36 | 49.861
2020-03-02 | 11:36 | 49.86
2020-03-02 | 11:36 | 49.86
2020-03-02 | 11:36 | 49.861
2020-03-02 | 11:36 | 49.862
2020-03-02 | 11:36 | 49.862
2020-03-02 | 11:36 | 49.863
2020-03-02 | 11:36 | 49.862
2020-03-02 | 11:36 | 49.862
2020-03-02 | 11:36 | 49.863
2020-03-02 | 11:36 | 49.863
2020-03-02 | 11:36 | 49.864
2020-03-02 | 11:36 | 49.865
2020-03-02 | 11:36 | 49.866
2020-03-02 | 11:36 | 49.866
2020-03-02 | 11:36 | 49.865
2020-03-02 | 11:36 | 49.866
2020-03-02 | 11:36 | 49.864
2020-03-02 | 11:36 | 49.862
2020-03-02 | 11:37 | 49.859
2020-03-02 | 11:37 | 49.855
2020-03-02 | 11:37 | 49.854
2020-03-02 | 11:37 | 49.854
2020-03-02 | 11:37 | 49.853
2020-03-02 | 11:37 | 49.853
2020-03-02 | 11:37 | 49.851
2020-03-02 | 11:37 | 49.85
2020-03-02 | 11:37 | 49.849
2020-03-02 | 11:37 | 49.85
2020-03-02 | 11:37 | 49.849
2020-03-02 | 11:37 | 49.849
2020-03-02 | 11:37 | 49.849
2020-03-02 | 11:37 | 49.849
2020-03-02 | 11:37 | 49.852
2020-03-02 | 11:37 | 49.855
2020-03-02 | 11:37 | 49.857
2020-03-02 | 11:37 | 49.86
2020-03-02 | 11:37 | 49.863
2020-03-02 | 11:37 | 49.864
2020-03-02 | 11:37 | 49.864
2020-03-02 | 11:37 | 49.861
2020-03-02 | 11:37 | 49.858
2020-03-02 | 11:37 | 49.853
2020-03-02 | 11:37 | 49.847
2020-03-02 | 11:37 | 49.844
2020-03-02 | 11:37 | 49.841
2020-03-02 | 11:37 | 49.84
2020-03-02 | 11:37 | 49.839
2020-03-02 | 11:37 | 49.837
2020-03-02 | 11:37 | 49.836
2020-03-02 | 11:37 | 49.836
2020-03-02 | 11:37 | 49.835
2020-03-02 | 11:37 | 49.838
2020-03-02 | 11:37 | 49.842
2020-03-02 | 11:37 | 49.845
2020-03-02 | 11:37 | 49.852
2020-03-02 | 11:37 | 49.857
2020-03-02 | 11:37 | 49.864
2020-03-02 | 11:37 | 49.872
2020-03-02 | 11:37 | 49.879
2020-03-02 | 11:37 | 49.886
2020-03-02 | 11:37 | 49.891
2020-03-02 | 11:37 | 49.896
2020-03-02 | 11:37 | 49.902
2020-03-02 | 11:37 | 49.907
2020-03-02 | 11:37 | 49.911
2020-03-02 | 11:37 | 49.913
2020-03-02 | 11:37 | 49.916
2020-03-02 | 11:37 | 49.918
2020-03-02 | 11:37 | 49.919
2020-03-02 | 11:37 | 49.92
2020-03-02 | 11:37 | 49.922
2020-03-02 | 11:37 | 49.923
2020-03-02 | 11:37 | 49.926
2020-03-02 | 11:37 | 49.929
2020-03-02 | 11:37 | 49.93
2020-03-02 | 11:37 | 49.932
2020-03-02 | 11:37 | 49.933
2020-03-02 | 11:38 | 49.933
2020-03-02 | 11:38 | 49.935
2020-03-02 | 11:38 | 49.938
2020-03-02 | 11:38 | 49.942
2020-03-02 | 11:38 | 49.944
2020-03-02 | 11:38 | 49.947
2020-03-02 | 11:38 | 49.948
2020-03-02 | 11:38 | 49.95
2020-03-02 | 11:38 | 49.953
2020-03-02 | 11:38 | 49.955
2020-03-02 | 11:38 | 49.958
2020-03-02 | 11:38 | 49.958
2020-03-02 | 11:38 | 49.96
2020-03-02 | 11:38 | 49.959
2020-03-02 | 11:38 | 49.957
2020-03-02 | 11:38 | 49.954
2020-03-02 | 11:38 | 49.952
2020-03-02 | 11:38 | 49.952
2020-03-02 | 11:38 | 49.949
2020-03-02 | 11:38 | 49.947
2020-03-02 | 11:38 | 49.945
2020-03-02 | 11:38 | 49.945
2020-03-02 | 11:38 | 49.944
2020-03-02 | 11:38 | 49.943
2020-03-02 | 11:38 | 49.941
2020-03-02 | 11:38 | 49.939
2020-03-02 | 11:38 | 49.937
2020-03-02 | 11:38 | 49.937
2020-03-02 | 11:38 | 49.936
2020-03-02 | 11:38 | 49.937
2020-03-02 | 11:38 | 49.936
2020-03-02 | 11:38 | 49.935
2020-03-02 | 11:38 | 49.935
2020-03-02 | 11:38 | 49.933
2020-03-02 | 11:38 | 49.933
2020-03-02 | 11:38 | 49.931
2020-03-02 | 11:38 | 49.93
2020-03-02 | 11:38 | 49.929
2020-03-02 | 11:38 | 49.93
2020-03-02 | 11:38 | 49.93
2020-03-02 | 11:38 | 49.931
2020-03-02 | 11:38 | 49.931
2020-03-02 | 11:38 | 49.93
2020-03-02 | 11:38 | 49.929
2020-03-02 | 11:38 | 49.93
2020-03-02 | 11:38 | 49.931
2020-03-02 | 11:38 | 49.93
2020-03-02 | 11:38 | 49.929
2020-03-02 | 11:38 | 49.928
2020-03-02 | 11:38 | 49.926
2020-03-02 | 11:38 | 49.923
2020-03-02 | 11:38 | 49.921
2020-03-02 | 11:38 | 49.918
2020-03-02 | 11:38 | 49.916
2020-03-02 | 11:38 | 49.916
2020-03-02 | 11:38 | 49.917
2020-03-02 | 11:38 | 49.917
2020-03-02 | 11:38 | 49.919
2020-03-02 | 11:38 | 49.921
2020-03-02 | 11:38 | 49.921
2020-03-02 | 11:39 | 49.923
2020-03-02 | 11:39 | 49.924
2020-03-02 | 11:39 | 49.927
2020-03-02 | 11:39 | 49.93
2020-03-02 | 11:39 | 49.931
2020-03-02 | 11:39 | 49.931
2020-03-02 | 11:39 | 49.932
2020-03-02 | 11:39 | 49.935
2020-03-02 | 11:39 | 49.934
2020-03-02 | 11:39 | 49.933
2020-03-02 | 11:39 | 49.932
2020-03-02 | 11:39 | 49.93
2020-03-02 | 11:39 | 49.928
2020-03-02 | 11:39 | 49.927
2020-03-02 | 11:39 | 49.926
2020-03-02 | 11:39 | 49.924
2020-03-02 | 11:39 | 49.925
2020-03-02 | 11:39 | 49.926
2020-03-02 | 11:39 | 49.924
2020-03-02 | 11:39 | 49.925
2020-03-02 | 11:39 | 49.925
2020-03-02 | 11:39 | 49.926
2020-03-02 | 11:39 | 49.924
2020-03-02 | 11:39 | 49.923
2020-03-02 | 11:39 | 49.92
2020-03-02 | 11:39 | 49.916
2020-03-02 | 11:39 | 49.912
2020-03-02 | 11:39 | 49.909
2020-03-02 | 11:39 | 49.909
2020-03-02 | 11:39 | 49.908
2020-03-02 | 11:39 | 49.908
2020-03-02 | 11:39 | 49.907
2020-03-02 | 11:39 | 49.906
2020-03-02 | 11:39 | 49.906
2020-03-02 | 11:39 | 49.905
2020-03-02 | 11:39 | 49.905
2020-03-02 | 11:39 | 49.904
2020-03-02 | 11:39 | 49.904
2020-03-02 | 11:39 | 49.903
2020-03-02 | 11:39 | 49.902
2020-03-02 | 11:39 | 49.903
2020-03-02 | 11:39 | 49.904
2020-03-02 | 11:39 | 49.904
2020-03-02 | 11:39 | 49.902
2020-03-02 | 11:39 | 49.903
2020-03-02 | 11:39 | 49.901
2020-03-02 | 11:39 | 49.903
2020-03-02 | 11:39 | 49.905
2020-03-02 | 11:39 | 49.903
2020-03-02 | 11:39 | 49.903
2020-03-02 | 11:39 | 49.899
2020-03-02 | 11:39 | 49.897
2020-03-02 | 11:39 | 49.894
2020-03-02 | 11:39 | 49.891
2020-03-02 | 11:39 | 49.889
2020-03-02 | 11:39 | 49.888
2020-03-02 | 11:39 | 49.888
2020-03-02 | 11:39 | 49.889
2020-03-02 | 11:39 | 49.888
2020-03-02 | 11:39 | 49.888
2020-03-02 | 11:40 | 49.889
2020-03-02 | 11:40 | 49.889
2020-03-02 | 11:40 | 49.887
2020-03-02 | 11:40 | 49.89
2020-03-02 | 11:40 | 49.89
2020-03-02 | 11:40 | 49.89
2020-03-02 | 11:40 | 49.887
2020-03-02 | 11:40 | 49.885
2020-03-02 | 11:40 | 49.883
2020-03-02 | 11:40 | 49.882
2020-03-02 | 11:40 | 49.881
2020-03-02 | 11:40 | 49.878
2020-03-02 | 11:40 | 49.875
2020-03-02 | 11:40 | 49.872
2020-03-02 | 11:40 | 49.87
2020-03-02 | 11:40 | 49.871
2020-03-02 | 11:40 | 49.871
2020-03-02 | 11:40 | 49.872
2020-03-02 | 11:40 | 49.876
2020-03-02 | 11:40 | 49.878
2020-03-02 | 11:40 | 49.88
2020-03-02 | 11:40 | 49.883
2020-03-02 | 11:40 | 49.888
2020-03-02 | 11:40 | 49.888
2020-03-02 | 11:40 | 49.889
2020-03-02 | 11:40 | 49.889
2020-03-02 | 11:40 | 49.891
2020-03-02 | 11:40 | 49.896
2020-03-02 | 11:40 | 49.898
2020-03-02 | 11:40 | 49.9
2020-03-02 | 11:40 | 49.901
2020-03-02 | 11:40 | 49.903
2020-03-02 | 11:40 | 49.902
2020-03-02 | 11:40 | 49.902
2020-03-02 | 11:40 | 49.901
2020-03-02 | 11:40 | 49.899
2020-03-02 | 11:40 | 49.898
2020-03-02 | 11:40 | 49.896
2020-03-02 | 11:40 | 49.892
2020-03-02 | 11:40 | 49.89
2020-03-02 | 11:40 | 49.886
2020-03-02 | 11:40 | 49.885
2020-03-02 | 11:40 | 49.885
2020-03-02 | 11:40 | 49.885
2020-03-02 | 11:40 | 49.883
2020-03-02 | 11:40 | 49.881
2020-03-02 | 11:40 | 49.877
2020-03-02 | 11:40 | 49.88
2020-03-02 | 11:40 | 49.879
2020-03-02 | 11:40 | 49.88
2020-03-02 | 11:40 | 49.882
2020-03-02 | 11:40 | 49.882
2020-03-02 | 11:40 | 49.884
2020-03-02 | 11:40 | 49.883
2020-03-02 | 11:40 | 49.884
2020-03-02 | 11:40 | 49.885
2020-03-02 | 11:40 | 49.885
2020-03-02 | 11:40 | 49.888
2020-03-02 | 11:40 | 49.888
2020-03-02 | 11:40 | 49.889
2020-03-02 | 11:41 | 49.891
2020-03-02 | 11:41 | 49.892
2020-03-02 | 11:41 | 49.893
2020-03-02 | 11:41 | 49.895
2020-03-02 | 11:41 | 49.898
2020-03-02 | 11:41 | 49.9
2020-03-02 | 11:41 | 49.901
2020-03-02 | 11:41 | 49.903
2020-03-02 | 11:41 | 49.906
2020-03-02 | 11:41 | 49.907
2020-03-02 | 11:41 | 49.908
2020-03-02 | 11:41 | 49.908
2020-03-02 | 11:41 | 49.91
2020-03-02 | 11:41 | 49.91
2020-03-02 | 11:41 | 49.911
2020-03-02 | 11:41 | 49.911
2020-03-02 | 11:41 | 49.913
2020-03-02 | 11:41 | 49.915
2020-03-02 | 11:41 | 49.915
2020-03-02 | 11:41 | 49.917
2020-03-02 | 11:41 | 49.916
2020-03-02 | 11:41 | 49.915
2020-03-02 | 11:41 | 49.915
2020-03-02 | 11:41 | 49.912
2020-03-02 | 11:41 | 49.913
2020-03-02 | 11:41 | 49.913
2020-03-02 | 11:41 | 49.916
2020-03-02 | 11:41 | 49.916
2020-03-02 | 11:41 | 49.916
2020-03-02 | 11:41 | 49.916
2020-03-02 | 11:41 | 49.917
2020-03-02 | 11:41 | 49.918
2020-03-02 | 11:41 | 49.92
2020-03-02 | 11:41 | 49.922
2020-03-02 | 11:41 | 49.926
2020-03-02 | 11:41 | 49.929
2020-03-02 | 11:41 | 49.931
2020-03-02 | 11:41 | 49.935
2020-03-02 | 11:41 | 49.94
2020-03-02 | 11:41 | 49.944
2020-03-02 | 11:41 | 49.948
2020-03-02 | 11:41 | 49.953
2020-03-02 | 11:41 | 49.955
2020-03-02 | 11:41 | 49.959
2020-03-02 | 11:41 | 49.96
2020-03-02 | 11:41 | 49.961
2020-03-02 | 11:41 | 49.963
2020-03-02 | 11:41 | 49.963
2020-03-02 | 11:41 | 49.965
2020-03-02 | 11:41 | 49.965
2020-03-02 | 11:41 | 49.967
2020-03-02 | 11:41 | 49.967
2020-03-02 | 11:41 | 49.968
2020-03-02 | 11:41 | 49.971
2020-03-02 | 11:41 | 49.972
2020-03-02 | 11:41 | 49.973
2020-03-02 | 11:41 | 49.973
2020-03-02 | 11:41 | 49.975
2020-03-02 | 11:41 | 49.975
2020-03-02 | 11:41 | 49.976
2020-03-02 | 11:42 | 49.978
2020-03-02 | 11:42 | 49.98
2020-03-02 | 11:42 | 49.982
2020-03-02 | 11:42 | 49.984
2020-03-02 | 11:42 | 49.983
2020-03-02 | 11:42 | 49.985
2020-03-02 | 11:42 | 49.984
2020-03-02 | 11:42 | 49.983
2020-03-02 | 11:42 | 49.985
2020-03-02 | 11:42 | 49.987
2020-03-02 | 11:42 | 49.99
2020-03-02 | 11:42 | 49.994
2020-03-02 | 11:42 | 49.994
2020-03-02 | 11:42 | 49.995
2020-03-02 | 11:42 | 49.997
2020-03-02 | 11:42 | 50
2020-03-02 | 11:42 | 50.003
2020-03-02 | 11:42 | 50.004
2020-03-02 | 11:42 | 50.006
2020-03-02 | 11:42 | 50.007
2020-03-02 | 11:42 | 50.007
2020-03-02 | 11:42 | 50.006
2020-03-02 | 11:42 | 50.009
2020-03-02 | 11:42 | 50.01
2020-03-02 | 11:42 | 50.012
2020-03-02 | 11:42 | 50.014
2020-03-02 | 11:42 | 50.013
2020-03-02 | 11:42 | 50.013
2020-03-02 | 11:42 | 50.013
2020-03-02 | 11:42 | 50.014

## Event 20200306-1
In UTC
Date | Time | Freq
2020-03-06 | 23:55 | 50.055
2020-03-06 | 23:55 | 50.052
2020-03-06 | 23:55 | 50.049
2020-03-06 | 23:55 | 50.046
2020-03-06 | 23:55 | 50.044
2020-03-06 | 23:55 | 50.044
2020-03-06 | 23:55 | 50.044
2020-03-06 | 23:55 | 50.045
2020-03-06 | 23:55 | 50.048
2020-03-06 | 23:55 | 50.049
2020-03-06 | 23:55 | 50.049
2020-03-06 | 23:55 | 50.05
2020-03-06 | 23:55 | 50.051
2020-03-06 | 23:55 | 50.05
2020-03-06 | 23:55 | 50.05
2020-03-06 | 23:55 | 50.05
2020-03-06 | 23:55 | 50.05
2020-03-06 | 23:55 | 50.051
2020-03-06 | 23:55 | 50.056
2020-03-06 | 23:55 | 50.06
2020-03-06 | 23:55 | 50.065
2020-03-06 | 23:55 | 50.068
2020-03-06 | 23:55 | 50.069
2020-03-06 | 23:55 | 50.071
2020-03-06 | 23:55 | 50.07
2020-03-06 | 23:55 | 50.071
2020-03-06 | 23:55 | 50.07
2020-03-06 | 23:55 | 50.066
2020-03-06 | 23:55 | 50.063
2020-03-06 | 23:55 | 50.057
2020-03-06 | 23:56 | 50.056
2020-03-06 | 23:56 | 50.056
2020-03-06 | 23:56 | 50.055
2020-03-06 | 23:56 | 50.055
2020-03-06 | 23:56 | 50.055
2020-03-06 | 23:56 | 50.054
2020-03-06 | 23:56 | 50.054
2020-03-06 | 23:56 | 50.054
2020-03-06 | 23:56 | 50.053
2020-03-06 | 23:56 | 50.051
2020-03-06 | 23:56 | 50.049
2020-03-06 | 23:56 | 50.046
2020-03-06 | 23:56 | 50.044
2020-03-06 | 23:56 | 50.04
2020-03-06 | 23:56 | 50.038
2020-03-06 | 23:56 | 50.037
2020-03-06 | 23:56 | 50.035
2020-03-06 | 23:56 | 50.035
2020-03-06 | 23:56 | 50.035
2020-03-06 | 23:56 | 50.034
2020-03-06 | 23:56 | 50.034
2020-03-06 | 23:56 | 50.034
2020-03-06 | 23:56 | 50.034
2020-03-06 | 23:56 | 50.036
2020-03-06 | 23:56 | 50.038
2020-03-06 | 23:56 | 50.038
2020-03-06 | 23:56 | 50.04
2020-03-06 | 23:56 | 50.012
2020-03-06 | 23:56 | 49.923
2020-03-06 | 23:56 | 49.84
2020-03-06 | 23:56 | 49.776
2020-03-06 | 23:56 | 49.733
2020-03-06 | 23:56 | 49.711
2020-03-06 | 23:56 | 49.696
2020-03-06 | 23:56 | 49.696
2020-03-06 | 23:56 | 49.702
2020-03-06 | 23:56 | 49.713
2020-03-06 | 23:56 | 49.725
2020-03-06 | 23:56 | 49.737
2020-03-06 | 23:56 | 49.747
2020-03-06 | 23:56 | 49.755
2020-03-06 | 23:56 | 49.759
2020-03-06 | 23:56 | 49.761
2020-03-06 | 23:56 | 49.761
2020-03-06 | 23:56 | 49.76
2020-03-06 | 23:56 | 49.761
2020-03-06 | 23:56 | 49.765
2020-03-06 | 23:56 | 49.769
2020-03-06 | 23:56 | 49.776
2020-03-06 | 23:56 | 49.788
2020-03-06 | 23:56 | 49.8
2020-03-06 | 23:56 | 49.813
2020-03-06 | 23:56 | 49.825
2020-03-06 | 23:56 | 49.835
2020-03-06 | 23:56 | 49.843
2020-03-06 | 23:56 | 49.851
2020-03-06 | 23:56 | 49.853
2020-03-06 | 23:56 | 49.853
2020-03-06 | 23:56 | 49.855
2020-03-06 | 23:56 | 49.852
2020-03-06 | 23:56 | 49.852
2020-03-06 | 23:57 | 49.854
2020-03-06 | 23:57 | 49.854
2020-03-06 | 23:57 | 49.855
2020-03-06 | 23:57 | 49.855
2020-03-06 | 23:57 | 49.857
2020-03-06 | 23:57 | 49.86
2020-03-06 | 23:57 | 49.862
2020-03-06 | 23:57 | 49.859
2020-03-06 | 23:57 | 49.859
2020-03-06 | 23:57 | 49.857
2020-03-06 | 23:57 | 49.855
2020-03-06 | 23:57 | 49.855
2020-03-06 | 23:57 | 49.853
2020-03-06 | 23:57 | 49.851
2020-03-06 | 23:57 | 49.852
2020-03-06 | 23:57 | 49.853
2020-03-06 | 23:57 | 49.852
2020-03-06 | 23:57 | 49.852
2020-03-06 | 23:57 | 49.851
2020-03-06 | 23:57 | 49.85
2020-03-06 | 23:57 | 49.848
2020-03-06 | 23:57 | 49.847
2020-03-06 | 23:57 | 49.842
2020-03-06 | 23:57 | 49.841
2020-03-06 | 23:57 | 49.84
2020-03-06 | 23:57 | 49.838
2020-03-06 | 23:57 | 49.836
2020-03-06 | 23:57 | 49.835
2020-03-06 | 23:57 | 49.835
2020-03-06 | 23:57 | 49.837
2020-03-06 | 23:57 | 49.838
2020-03-06 | 23:57 | 49.839
2020-03-06 | 23:57 | 49.843
2020-03-06 | 23:57 | 49.845
2020-03-06 | 23:57 | 49.846
2020-03-06 | 23:57 | 49.847
2020-03-06 | 23:57 | 49.847
2020-03-06 | 23:57 | 49.845
2020-03-06 | 23:57 | 49.844
2020-03-06 | 23:57 | 49.843
2020-03-06 | 23:57 | 49.841
2020-03-06 | 23:57 | 49.839
2020-03-06 | 23:57 | 49.838
2020-03-06 | 23:57 | 49.837
2020-03-06 | 23:57 | 49.835
2020-03-06 | 23:57 | 49.834
2020-03-06 | 23:57 | 49.833
2020-03-06 | 23:57 | 49.832
2020-03-06 | 23:57 | 49.833
2020-03-06 | 23:57 | 49.83
2020-03-06 | 23:57 | 49.83
2020-03-06 | 23:57 | 49.829
2020-03-06 | 23:57 | 49.829
2020-03-06 | 23:57 | 49.829
2020-03-06 | 23:57 | 49.829
2020-03-06 | 23:57 | 49.829
2020-03-06 | 23:57 | 49.831
2020-03-06 | 23:57 | 49.834
2020-03-06 | 23:57 | 49.836
2020-03-06 | 23:58 | 49.842
2020-03-06 | 23:58 | 49.847
2020-03-06 | 23:58 | 49.853
2020-03-06 | 23:58 | 49.858
2020-03-06 | 23:58 | 49.861
2020-03-06 | 23:58 | 49.864
2020-03-06 | 23:58 | 49.867
2020-03-06 | 23:58 | 49.866
2020-03-06 | 23:58 | 49.868
2020-03-06 | 23:58 | 49.87
2020-03-06 | 23:58 | 49.872
2020-03-06 | 23:58 | 49.872
2020-03-06 | 23:58 | 49.873
2020-03-06 | 23:58 | 49.874
2020-03-06 | 23:58 | 49.874
2020-03-06 | 23:58 | 49.879
2020-03-06 | 23:58 | 49.881
2020-03-06 | 23:58 | 49.884
2020-03-06 | 23:58 | 49.886
2020-03-06 | 23:58 | 49.889
2020-03-06 | 23:58 | 49.891
2020-03-06 | 23:58 | 49.891
2020-03-06 | 23:58 | 49.891
2020-03-06 | 23:58 | 49.89
2020-03-06 | 23:58 | 49.89
2020-03-06 | 23:58 | 49.888
2020-03-06 | 23:58 | 49.888
2020-03-06 | 23:58 | 49.89
2020-03-06 | 23:58 | 49.888
2020-03-06 | 23:58 | 49.889
2020-03-06 | 23:58 | 49.887
2020-03-06 | 23:58 | 49.885
2020-03-06 | 23:58 | 49.883
2020-03-06 | 23:58 | 49.882
2020-03-06 | 23:58 | 49.881
2020-03-06 | 23:58 | 49.883
2020-03-06 | 23:58 | 49.884
2020-03-06 | 23:58 | 49.887
2020-03-06 | 23:58 | 49.889
2020-03-06 | 23:58 | 49.891
2020-03-06 | 23:58 | 49.893
2020-03-06 | 23:58 | 49.893
2020-03-06 | 23:58 | 49.892
2020-03-06 | 23:58 | 49.892
2020-03-06 | 23:58 | 49.892
2020-03-06 | 23:58 | 49.892
2020-03-06 | 23:58 | 49.893
2020-03-06 | 23:58 | 49.894
2020-03-06 | 23:58 | 49.895
2020-03-06 | 23:58 | 49.898
2020-03-06 | 23:58 | 49.899
2020-03-06 | 23:58 | 49.902
2020-03-06 | 23:58 | 49.905
2020-03-06 | 23:58 | 49.907
2020-03-06 | 23:58 | 49.909
2020-03-06 | 23:58 | 49.911
2020-03-06 | 23:58 | 49.913
2020-03-06 | 23:58 | 49.914
2020-03-06 | 23:58 | 49.917
2020-03-06 | 23:58 | 49.918
2020-03-06 | 23:58 | 49.919
2020-03-06 | 23:59 | 49.923
2020-03-06 | 23:59 | 49.926
2020-03-06 | 23:59 | 49.926
2020-03-06 | 23:59 | 49.926
2020-03-06 | 23:59 | 49.926
2020-03-06 | 23:59 | 49.926
2020-03-06 | 23:59 | 49.926
2020-03-06 | 23:59 | 49.927
2020-03-06 | 23:59 | 49.928
2020-03-06 | 23:59 | 49.927
2020-03-06 | 23:59 | 49.925
2020-03-06 | 23:59 | 49.924
2020-03-06 | 23:59 | 49.922
2020-03-06 | 23:59 | 49.923
2020-03-06 | 23:59 | 49.925
2020-03-06 | 23:59 | 49.926
2020-03-06 | 23:59 | 49.928
2020-03-06 | 23:59 | 49.929
2020-03-06 | 23:59 | 49.93
2020-03-06 | 23:59 | 49.929
2020-03-06 | 23:59 | 49.928
2020-03-06 | 23:59 | 49.926
2020-03-06 | 23:59 | 49.924
2020-03-06 | 23:59 | 49.922
2020-03-06 | 23:59 | 49.922
2020-03-06 | 23:59 | 49.923
2020-03-06 | 23:59 | 49.923
2020-03-06 | 23:59 | 49.923
2020-03-06 | 23:59 | 49.926
2020-03-06 | 23:59 | 49.928
2020-03-06 | 23:59 | 49.927
2020-03-06 | 23:59 | 49.927
2020-03-06 | 23:59 | 49.928
2020-03-06 | 23:59 | 49.927
2020-03-06 | 23:59 | 49.926
2020-03-06 | 23:59 | 49.924
2020-03-06 | 23:59 | 49.923
2020-03-06 | 23:59 | 49.922
2020-03-06 | 23:59 | 49.922
2020-03-06 | 23:59 | 49.918
2020-03-06 | 23:59 | 49.919
2020-03-06 | 23:59 | 49.917
2020-03-06 | 23:59 | 49.916
2020-03-06 | 23:59 | 49.917
2020-03-06 | 23:59 | 49.919
2020-03-06 | 23:59 | 49.919
2020-03-06 | 23:59 | 49.92
2020-03-06 | 23:59 | 49.921
2020-03-06 | 23:59 | 49.923
2020-03-06 | 23:59 | 49.922
2020-03-06 | 23:59 | 49.922
2020-03-06 | 23:59 | 49.922
2020-03-06 | 23:59 | 49.922
2020-03-06 | 23:59 | 49.922
2020-03-06 | 23:59 | 49.922
2020-03-06 | 23:59 | 49.922
2020-03-06 | 23:59 | 49.921
2020-03-06 | 23:59 | 49.921
2020-03-06 | 23:59 | 49.922
2020-03-06 | 24:00 | 49.92
2020-03-06 | 24:00 | 49.92
2020-03-06 | 24:00 | 49.921
2020-03-06 | 24:00 | 49.922
2020-03-06 | 24:00 | 49.922
2020-03-06 | 24:00 | 49.924
2020-03-06 | 24:00 | 49.924
2020-03-06 | 24:00 | 49.924
2020-03-06 | 24:00 | 49.925
2020-03-06 | 24:00 | 49.925
2020-03-06 | 24:00 | 49.925
2020-03-06 | 24:00 | 49.924
2020-03-06 | 24:00 | 49.923
2020-03-06 | 24:00 | 49.924
2020-03-06 | 24:00 | 49.926
2020-03-06 | 24:00 | 49.928
2020-03-06 | 24:00 | 49.928
2020-03-06 | 24:00 | 49.932
2020-03-06 | 24:00 | 49.933
2020-03-06 | 24:00 | 49.931
2020-03-06 | 24:00 | 49.931
2020-03-06 | 24:00 | 49.928
2020-03-06 | 24:00 | 49.926
2020-03-06 | 24:00 | 49.926
2020-03-06 | 24:00 | 49.926
2020-03-06 | 24:00 | 49.924
2020-03-06 | 24:00 | 49.924
2020-03-06 | 24:00 | 49.922
2020-03-06 | 24:00 | 49.921
2020-03-06 | 24:00 | 49.919
2020-03-07 | 0:00 | 49.913
2020-03-07 | 0:00 | 49.906
2020-03-07 | 0:00 | 49.9
2020-03-07 | 0:00 | 49.893
2020-03-07 | 0:00 | 49.884
2020-03-07 | 0:00 | 49.878
2020-03-07 | 0:00 | 49.874
2020-03-07 | 0:00 | 49.869
2020-03-07 | 0:00 | 49.867
2020-03-07 | 0:00 | 49.864
2020-03-07 | 0:00 | 49.863
2020-03-07 | 0:00 | 49.863
2020-03-07 | 0:00 | 49.865
2020-03-07 | 0:00 | 49.868
2020-03-07 | 0:00 | 49.871
2020-03-07 | 0:00 | 49.873
2020-03-07 | 0:00 | 49.877
2020-03-07 | 0:00 | 49.879
2020-03-07 | 0:00 | 49.881
2020-03-07 | 0:00 | 49.882
2020-03-07 | 0:00 | 49.88
2020-03-07 | 0:00 | 49.879
2020-03-07 | 0:00 | 49.879
2020-03-07 | 0:00 | 49.879
2020-03-07 | 0:00 | 49.878
2020-03-07 | 0:00 | 49.878
2020-03-07 | 0:00 | 49.877
2020-03-07 | 0:00 | 49.876
2020-03-07 | 0:00 | 49.877
2020-03-07 | 0:00 | 49.877
2020-03-07 | 0:00 | 49.875
2020-03-07 | 0:01 | 49.873
2020-03-07 | 0:01 | 49.873
2020-03-07 | 0:01 | 49.873
2020-03-07 | 0:01 | 49.874
2020-03-07 | 0:01 | 49.874
2020-03-07 | 0:01 | 49.874
2020-03-07 | 0:01 | 49.875
2020-03-07 | 0:01 | 49.875
2020-03-07 | 0:01 | 49.876
2020-03-07 | 0:01 | 49.875
2020-03-07 | 0:01 | 49.874
2020-03-07 | 0:01 | 49.872
2020-03-07 | 0:01 | 49.872
2020-03-07 | 0:01 | 49.873
2020-03-07 | 0:01 | 49.872
2020-03-07 | 0:01 | 49.872
2020-03-07 | 0:01 | 49.873
2020-03-07 | 0:01 | 49.874
2020-03-07 | 0:01 | 49.876
2020-03-07 | 0:01 | 49.877
2020-03-07 | 0:01 | 49.878
2020-03-07 | 0:01 | 49.876
2020-03-07 | 0:01 | 49.874
2020-03-07 | 0:01 | 49.873
2020-03-07 | 0:01 | 49.873
2020-03-07 | 0:01 | 49.872
2020-03-07 | 0:01 | 49.874
2020-03-07 | 0:01 | 49.874
2020-03-07 | 0:01 | 49.874
2020-03-07 | 0:01 | 49.874
2020-03-07 | 0:01 | 49.873
2020-03-07 | 0:01 | 49.872
2020-03-07 | 0:01 | 49.872
2020-03-07 | 0:01 | 49.872
2020-03-07 | 0:01 | 49.871
2020-03-07 | 0:01 | 49.873
2020-03-07 | 0:01 | 49.874
2020-03-07 | 0:01 | 49.873
2020-03-07 | 0:01 | 49.872
2020-03-07 | 0:01 | 49.872
2020-03-07 | 0:01 | 49.869
2020-03-07 | 0:01 | 49.867
2020-03-07 | 0:01 | 49.867
2020-03-07 | 0:01 | 49.866
2020-03-07 | 0:01 | 49.864
2020-03-07 | 0:01 | 49.864
2020-03-07 | 0:01 | 49.864
2020-03-07 | 0:01 | 49.864
2020-03-07 | 0:01 | 49.864
2020-03-07 | 0:01 | 49.865
2020-03-07 | 0:01 | 49.866
2020-03-07 | 0:01 | 49.867
2020-03-07 | 0:01 | 49.869
2020-03-07 | 0:01 | 49.872
2020-03-07 | 0:01 | 49.874
2020-03-07 | 0:01 | 49.877
2020-03-07 | 0:01 | 49.878
2020-03-07 | 0:01 | 49.88
2020-03-07 | 0:01 | 49.881
2020-03-07 | 0:02 | 49.884
2020-03-07 | 0:02 | 49.886
2020-03-07 | 0:02 | 49.888
2020-03-07 | 0:02 | 49.889
2020-03-07 | 0:02 | 49.889
2020-03-07 | 0:02 | 49.891
2020-03-07 | 0:02 | 49.892
2020-03-07 | 0:02 | 49.892
2020-03-07 | 0:02 | 49.891
2020-03-07 | 0:02 | 49.891
2020-03-07 | 0:02 | 49.89
2020-03-07 | 0:02 | 49.889
2020-03-07 | 0:02 | 49.889
2020-03-07 | 0:02 | 49.89
2020-03-07 | 0:02 | 49.891
2020-03-07 | 0:02 | 49.891
2020-03-07 | 0:02 | 49.891
2020-03-07 | 0:02 | 49.891
2020-03-07 | 0:02 | 49.888
2020-03-07 | 0:02 | 49.885
2020-03-07 | 0:02 | 49.882
2020-03-07 | 0:02 | 49.882
2020-03-07 | 0:02 | 49.882
2020-03-07 | 0:02 | 49.883
2020-03-07 | 0:02 | 49.884
2020-03-07 | 0:02 | 49.886
2020-03-07 | 0:02 | 49.887
2020-03-07 | 0:02 | 49.887
2020-03-07 | 0:02 | 49.889
2020-03-07 | 0:02 | 49.891
2020-03-07 | 0:02 | 49.891
2020-03-07 | 0:02 | 49.891
2020-03-07 | 0:02 | 49.892
2020-03-07 | 0:02 | 49.891
2020-03-07 | 0:02 | 49.888
2020-03-07 | 0:02 | 49.888
2020-03-07 | 0:02 | 49.888
2020-03-07 | 0:02 | 49.888
2020-03-07 | 0:02 | 49.889
2020-03-07 | 0:02 | 49.891
2020-03-07 | 0:02 | 49.891
2020-03-07 | 0:02 | 49.89
2020-03-07 | 0:02 | 49.889
2020-03-07 | 0:02 | 49.89
2020-03-07 | 0:02 | 49.891
2020-03-07 | 0:02 | 49.892
2020-03-07 | 0:02 | 49.893
2020-03-07 | 0:02 | 49.893
2020-03-07 | 0:02 | 49.893
2020-03-07 | 0:02 | 49.893
2020-03-07 | 0:02 | 49.894
2020-03-07 | 0:02 | 49.894
2020-03-07 | 0:02 | 49.893
2020-03-07 | 0:02 | 49.896
2020-03-07 | 0:02 | 49.898
2020-03-07 | 0:02 | 49.9
2020-03-07 | 0:02 | 49.902
2020-03-07 | 0:02 | 49.902
2020-03-07 | 0:02 | 49.902
2020-03-07 | 0:02 | 49.9
2020-03-07 | 0:02 | 49.898
2020-03-07 | 0:03 | 49.897
2020-03-07 | 0:03 | 49.893
2020-03-07 | 0:03 | 49.892
2020-03-07 | 0:03 | 49.891
2020-03-07 | 0:03 | 49.89
2020-03-07 | 0:03 | 49.892
2020-03-07 | 0:03 | 49.891
2020-03-07 | 0:03 | 49.891
2020-03-07 | 0:03 | 49.891
2020-03-07 | 0:03 | 49.891
2020-03-07 | 0:03 | 49.894
2020-03-07 | 0:03 | 49.898
2020-03-07 | 0:03 | 49.898
2020-03-07 | 0:03 | 49.899
2020-03-07 | 0:03 | 49.9
2020-03-07 | 0:03 | 49.902
2020-03-07 | 0:03 | 49.907
2020-03-07 | 0:03 | 49.913
2020-03-07 | 0:03 | 49.917
2020-03-07 | 0:03 | 49.922
2020-03-07 | 0:03 | 49.927
2020-03-07 | 0:03 | 49.929
2020-03-07 | 0:03 | 49.93
2020-03-07 | 0:03 | 49.931
2020-03-07 | 0:03 | 49.931
2020-03-07 | 0:03 | 49.931
2020-03-07 | 0:03 | 49.932
2020-03-07 | 0:03 | 49.932
2020-03-07 | 0:03 | 49.931
2020-03-07 | 0:03 | 49.93
2020-03-07 | 0:03 | 49.928
2020-03-07 | 0:03 | 49.927
2020-03-07 | 0:03 | 49.926
2020-03-07 | 0:03 | 49.926
2020-03-07 | 0:03 | 49.925
2020-03-07 | 0:03 | 49.925
2020-03-07 | 0:03 | 49.926
2020-03-07 | 0:03 | 49.926
2020-03-07 | 0:03 | 49.927
2020-03-07 | 0:03 | 49.931
2020-03-07 | 0:03 | 49.933
2020-03-07 | 0:03 | 49.933
2020-03-07 | 0:03 | 49.935
2020-03-07 | 0:03 | 49.936
2020-03-07 | 0:03 | 49.936
2020-03-07 | 0:03 | 49.938
2020-03-07 | 0:03 | 49.94
2020-03-07 | 0:03 | 49.941
2020-03-07 | 0:03 | 49.941
2020-03-07 | 0:03 | 49.941
2020-03-07 | 0:03 | 49.939
2020-03-07 | 0:03 | 49.94
2020-03-07 | 0:03 | 49.94
2020-03-07 | 0:03 | 49.941
2020-03-07 | 0:03 | 49.941
2020-03-07 | 0:03 | 49.939
2020-03-07 | 0:03 | 49.939
2020-03-07 | 0:03 | 49.939
2020-03-07 | 0:03 | 49.939
2020-03-07 | 0:04 | 49.94
2020-03-07 | 0:04 | 49.941
2020-03-07 | 0:04 | 49.941
2020-03-07 | 0:04 | 49.942
2020-03-07 | 0:04 | 49.941
2020-03-07 | 0:04 | 49.941
2020-03-07 | 0:04 | 49.941
2020-03-07 | 0:04 | 49.942
2020-03-07 | 0:04 | 49.943
2020-03-07 | 0:04 | 49.943
2020-03-07 | 0:04 | 49.946
2020-03-07 | 0:04 | 49.947
2020-03-07 | 0:04 | 49.949
2020-03-07 | 0:04 | 49.954
2020-03-07 | 0:04 | 49.956
2020-03-07 | 0:04 | 49.958
2020-03-07 | 0:04 | 49.962
2020-03-07 | 0:04 | 49.965
2020-03-07 | 0:04 | 49.969
2020-03-07 | 0:04 | 49.973
2020-03-07 | 0:04 | 49.976
2020-03-07 | 0:04 | 49.98
2020-03-07 | 0:04 | 49.984
2020-03-07 | 0:04 | 49.987
2020-03-07 | 0:04 | 49.987
2020-03-07 | 0:04 | 49.986
2020-03-07 | 0:04 | 49.987
2020-03-07 | 0:04 | 49.985
2020-03-07 | 0:04 | 49.985
2020-03-07 | 0:04 | 49.984
2020-03-07 | 0:04 | 49.98
2020-03-07 | 0:04 | 49.979
2020-03-07 | 0:04 | 49.977
2020-03-07 | 0:04 | 49.977
2020-03-07 | 0:04 | 49.977
2020-03-07 | 0:04 | 49.977
2020-03-07 | 0:04 | 49.977
2020-03-07 | 0:04 | 49.976
2020-03-07 | 0:04 | 49.979
2020-03-07 | 0:04 | 49.981
2020-03-07 | 0:04 | 49.983
2020-03-07 | 0:04 | 49.984
2020-03-07 | 0:04 | 49.986
2020-03-07 | 0:04 | 49.988
2020-03-07 | 0:04 | 49.986
2020-03-07 | 0:04 | 49.985
2020-03-07 | 0:04 | 49.985
2020-03-07 | 0:04 | 49.986
2020-03-07 | 0:04 | 49.984
2020-03-07 | 0:04 | 49.983
2020-03-07 | 0:04 | 49.983
2020-03-07 | 0:04 | 49.984
2020-03-07 | 0:04 | 49.985
2020-03-07 | 0:04 | 49.986
2020-03-07 | 0:04 | 49.989
2020-03-07 | 0:04 | 49.989
2020-03-07 | 0:04 | 49.99
2020-03-07 | 0:04 | 49.988
2020-03-07 | 0:04 | 49.988
2020-03-07 | 0:04 | 49.988
2020-03-07 | 0:04 | 49.988
2020-03-07 | 0:05 | 49.989
2020-03-07 | 0:05 | 49.988
2020-03-07 | 0:05 | 49.989
2020-03-07 | 0:05 | 49.99
2020-03-07 | 0:05 | 49.991
2020-03-07 | 0:05 | 49.993
2020-03-07 | 0:05 | 49.994
2020-03-07 | 0:05 | 49.997
2020-03-07 | 0:05 | 49.997
2020-03-07 | 0:05 | 49.997
2020-03-07 | 0:05 | 49.998
2020-03-07 | 0:05 | 49.998
2020-03-07 | 0:05 | 49.999
2020-03-07 | 0:05 | 50
2020-03-07 | 0:05 | 49.999
2020-03-07 | 0:05 | 49.999
2020-03-07 | 0:05 | 50
2020-03-07 | 0:05 | 50.002
2020-03-07 | 0:05 | 50.004
2020-03-07 | 0:05 | 50.006
2020-03-07 | 0:05 | 50.008
2020-03-07 | 0:05 | 50.007
2020-03-07 | 0:05 | 50.009
2020-03-07 | 0:05 | 50.009
2020-03-07 | 0:05 | 50.01
2020-03-07 | 0:05 | 50.011
2020-03-07 | 0:05 | 50.012
2020-03-07 | 0:05 | 50.011
2020-03-07 | 0:05 | 50.012

## Event 20200307-1
In UTC
Date | Time | Freq
2020-03-07 | 1:04 | 49.973
2020-03-07 | 1:04 | 49.971
2020-03-07 | 1:04 | 49.972
2020-03-07 | 1:04 | 49.972
2020-03-07 | 1:04 | 49.974
2020-03-07 | 1:04 | 49.978
2020-03-07 | 1:04 | 49.98
2020-03-07 | 1:04 | 49.98
2020-03-07 | 1:04 | 49.979
2020-03-07 | 1:04 | 49.978
2020-03-07 | 1:04 | 49.975
2020-03-07 | 1:04 | 49.972
2020-03-07 | 1:04 | 49.968
2020-03-07 | 1:04 | 49.963
2020-03-07 | 1:04 | 49.96
2020-03-07 | 1:04 | 49.957
2020-03-07 | 1:04 | 49.955
2020-03-07 | 1:04 | 49.957
2020-03-07 | 1:04 | 49.959
2020-03-07 | 1:04 | 49.961
2020-03-07 | 1:04 | 49.961
2020-03-07 | 1:04 | 49.963
2020-03-07 | 1:04 | 49.964
2020-03-07 | 1:04 | 49.967
2020-03-07 | 1:04 | 49.972
2020-03-07 | 1:04 | 49.973
2020-03-07 | 1:04 | 49.972
2020-03-07 | 1:04 | 49.971
2020-03-07 | 1:04 | 49.97
2020-03-07 | 1:04 | 49.968
2020-03-07 | 1:04 | 49.966
2020-03-07 | 1:05 | 49.966
2020-03-07 | 1:05 | 49.967
2020-03-07 | 1:05 | 49.969
2020-03-07 | 1:05 | 49.97
2020-03-07 | 1:05 | 49.974
2020-03-07 | 1:05 | 49.976
2020-03-07 | 1:05 | 49.976
2020-03-07 | 1:05 | 49.979
2020-03-07 | 1:05 | 49.979
2020-03-07 | 1:05 | 49.982
2020-03-07 | 1:05 | 49.983
2020-03-07 | 1:05 | 49.981
2020-03-07 | 1:05 | 49.981
2020-03-07 | 1:05 | 49.98
2020-03-07 | 1:05 | 49.98
2020-03-07 | 1:05 | 49.979
2020-03-07 | 1:05 | 49.977
2020-03-07 | 1:05 | 49.978
2020-03-07 | 1:05 | 49.979
2020-03-07 | 1:05 | 49.979
2020-03-07 | 1:05 | 49.981
2020-03-07 | 1:05 | 49.984
2020-03-07 | 1:05 | 49.988
2020-03-07 | 1:05 | 49.99
2020-03-07 | 1:05 | 49.991
2020-03-07 | 1:05 | 49.991
2020-03-07 | 1:05 | 49.995
2020-03-07 | 1:05 | 49.997
2020-03-07 | 1:05 | 49.999
2020-03-07 | 1:05 | 50.003
2020-03-07 | 1:05 | 50.003
2020-03-07 | 1:05 | 50.003
2020-03-07 | 1:05 | 50.001
2020-03-07 | 1:05 | 50.006
2020-03-07 | 1:05 | 50.01
2020-03-07 | 1:05 | 50.01
2020-03-07 | 1:05 | 50.013
2020-03-07 | 1:05 | 50.018
2020-03-07 | 1:05 | 50.02
2020-03-07 | 1:05 | 50.024
2020-03-07 | 1:05 | 50.026
2020-03-07 | 1:05 | 50.026
2020-03-07 | 1:05 | 50.026
2020-03-07 | 1:05 | 50.027
2020-03-07 | 1:05 | 50.03
2020-03-07 | 1:05 | 50.029
2020-03-07 | 1:05 | 50.031
2020-03-07 | 1:05 | 50.028
2020-03-07 | 1:05 | 50.027
2020-03-07 | 1:05 | 50.023
2020-03-07 | 1:05 | 50.022
2020-03-07 | 1:05 | 50.021
2020-03-07 | 1:05 | 50.021
2020-03-07 | 1:05 | 50.022
2020-03-07 | 1:05 | 50.022
2020-03-07 | 1:05 | 50.022
2020-03-07 | 1:05 | 50.024
2020-03-07 | 1:05 | 50.02
2020-03-07 | 1:05 | 50.018
2020-03-07 | 1:06 | 50.018
2020-03-07 | 1:06 | 50.017
2020-03-07 | 1:06 | 50.017
2020-03-07 | 1:06 | 50.016
2020-03-07 | 1:06 | 50.019
2020-03-07 | 1:06 | 50.021
2020-03-07 | 1:06 | 50.02
2020-03-07 | 1:06 | 50.021
2020-03-07 | 1:06 | 50.02
2020-03-07 | 1:06 | 50.018
2020-03-07 | 1:06 | 50.016
2020-03-07 | 1:06 | 50.014
2020-03-07 | 1:06 | 50.015
2020-03-07 | 1:06 | 50.013
2020-03-07 | 1:06 | 50.01
2020-03-07 | 1:06 | 50.008
2020-03-07 | 1:06 | 50.005
2020-03-07 | 1:06 | 50.002
2020-03-07 | 1:06 | 50.002
2020-03-07 | 1:06 | 50.005
2020-03-07 | 1:06 | 50.005
2020-03-07 | 1:06 | 50.007
2020-03-07 | 1:06 | 50.002
2020-03-07 | 1:06 | 49.971
2020-03-07 | 1:06 | 49.941
2020-03-07 | 1:06 | 49.914
2020-03-07 | 1:06 | 49.898
2020-03-07 | 1:06 | 49.882
2020-03-07 | 1:06 | 49.862
2020-03-07 | 1:06 | 49.848
2020-03-07 | 1:06 | 49.842
2020-03-07 | 1:06 | 49.844
2020-03-07 | 1:06 | 49.846
2020-03-07 | 1:06 | 49.848
2020-03-07 | 1:06 | 49.851
2020-03-07 | 1:06 | 49.855
2020-03-07 | 1:06 | 49.858
2020-03-07 | 1:06 | 49.859
2020-03-07 | 1:06 | 49.861
2020-03-07 | 1:06 | 49.861
2020-03-07 | 1:06 | 49.859
2020-03-07 | 1:06 | 49.856
2020-03-07 | 1:06 | 49.853
2020-03-07 | 1:06 | 49.851
2020-03-07 | 1:06 | 49.851
2020-03-07 | 1:06 | 49.85
2020-03-07 | 1:06 | 49.85
2020-03-07 | 1:06 | 49.85
2020-03-07 | 1:06 | 49.853
2020-03-07 | 1:06 | 49.855
2020-03-07 | 1:06 | 49.858
2020-03-07 | 1:06 | 49.858
2020-03-07 | 1:06 | 49.857
2020-03-07 | 1:06 | 49.858
2020-03-07 | 1:06 | 49.859
2020-03-07 | 1:06 | 49.856
2020-03-07 | 1:06 | 49.853
2020-03-07 | 1:06 | 49.852
2020-03-07 | 1:06 | 49.847
2020-03-07 | 1:06 | 49.847
2020-03-07 | 1:06 | 49.847
2020-03-07 | 1:07 | 49.846
2020-03-07 | 1:07 | 49.846
2020-03-07 | 1:07 | 49.848
2020-03-07 | 1:07 | 49.849
2020-03-07 | 1:07 | 49.849
2020-03-07 | 1:07 | 49.849
2020-03-07 | 1:07 | 49.849
2020-03-07 | 1:07 | 49.846
2020-03-07 | 1:07 | 49.848
2020-03-07 | 1:07 | 49.848
2020-03-07 | 1:07 | 49.847
2020-03-07 | 1:07 | 49.847
2020-03-07 | 1:07 | 49.849
2020-03-07 | 1:07 | 49.848
2020-03-07 | 1:07 | 49.848
2020-03-07 | 1:07 | 49.848
2020-03-07 | 1:07 | 49.848
2020-03-07 | 1:07 | 49.849
2020-03-07 | 1:07 | 49.85
2020-03-07 | 1:07 | 49.849
2020-03-07 | 1:07 | 49.849
2020-03-07 | 1:07 | 49.85
2020-03-07 | 1:07 | 49.85
2020-03-07 | 1:07 | 49.851
2020-03-07 | 1:07 | 49.853
2020-03-07 | 1:07 | 49.856
2020-03-07 | 1:07 | 49.856
2020-03-07 | 1:07 | 49.855
2020-03-07 | 1:07 | 49.858
2020-03-07 | 1:07 | 49.856
2020-03-07 | 1:07 | 49.857
2020-03-07 | 1:07 | 49.858
2020-03-07 | 1:07 | 49.858
2020-03-07 | 1:07 | 49.859
2020-03-07 | 1:07 | 49.861
2020-03-07 | 1:07 | 49.862
2020-03-07 | 1:07 | 49.862
2020-03-07 | 1:07 | 49.862
2020-03-07 | 1:07 | 49.863
2020-03-07 | 1:07 | 49.865
2020-03-07 | 1:07 | 49.864
2020-03-07 | 1:07 | 49.865
2020-03-07 | 1:07 | 49.867
2020-03-07 | 1:07 | 49.869
2020-03-07 | 1:07 | 49.873
2020-03-07 | 1:07 | 49.877
2020-03-07 | 1:07 | 49.882
2020-03-07 | 1:07 | 49.887
2020-03-07 | 1:07 | 49.895
2020-03-07 | 1:07 | 49.903
2020-03-07 | 1:07 | 49.911
2020-03-07 | 1:07 | 49.914
2020-03-07 | 1:07 | 49.918
2020-03-07 | 1:07 | 49.921
2020-03-07 | 1:07 | 49.922
2020-03-07 | 1:07 | 49.924
2020-03-07 | 1:07 | 49.926
2020-03-07 | 1:07 | 49.926
2020-03-07 | 1:07 | 49.926
2020-03-07 | 1:08 | 49.924
2020-03-07 | 1:08 | 49.924
2020-03-07 | 1:08 | 49.925
2020-03-07 | 1:08 | 49.924
2020-03-07 | 1:08 | 49.924
2020-03-07 | 1:08 | 49.921
2020-03-07 | 1:08 | 49.919
2020-03-07 | 1:08 | 49.919
2020-03-07 | 1:08 | 49.92
2020-03-07 | 1:08 | 49.921
2020-03-07 | 1:08 | 49.921
2020-03-07 | 1:08 | 49.921
2020-03-07 | 1:08 | 49.921
2020-03-07 | 1:08 | 49.918
2020-03-07 | 1:08 | 49.916
2020-03-07 | 1:08 | 49.918
2020-03-07 | 1:08 | 49.923
2020-03-07 | 1:08 | 49.927
2020-03-07 | 1:08 | 49.928
2020-03-07 | 1:08 | 49.929
2020-03-07 | 1:08 | 49.931
2020-03-07 | 1:08 | 49.933
2020-03-07 | 1:08 | 49.934
2020-03-07 | 1:08 | 49.936
2020-03-07 | 1:08 | 49.939
2020-03-07 | 1:08 | 49.94
2020-03-07 | 1:08 | 49.939
2020-03-07 | 1:08 | 49.939
2020-03-07 | 1:08 | 49.939
2020-03-07 | 1:08 | 49.938
2020-03-07 | 1:08 | 49.935
2020-03-07 | 1:08 | 49.934
2020-03-07 | 1:08 | 49.934
2020-03-07 | 1:08 | 49.934
2020-03-07 | 1:08 | 49.936
2020-03-07 | 1:08 | 49.94
2020-03-07 | 1:08 | 49.944
2020-03-07 | 1:08 | 49.95
2020-03-07 | 1:08 | 49.953
2020-03-07 | 1:08 | 49.957
2020-03-07 | 1:08 | 49.959
2020-03-07 | 1:08 | 49.96
2020-03-07 | 1:08 | 49.961
2020-03-07 | 1:08 | 49.961
2020-03-07 | 1:08 | 49.963
2020-03-07 | 1:08 | 49.967
2020-03-07 | 1:08 | 49.972
2020-03-07 | 1:08 | 49.975
2020-03-07 | 1:08 | 49.979
2020-03-07 | 1:08 | 49.981
2020-03-07 | 1:08 | 49.981
2020-03-07 | 1:08 | 49.981
2020-03-07 | 1:08 | 49.981
2020-03-07 | 1:08 | 49.981
2020-03-07 | 1:08 | 49.98
2020-03-07 | 1:08 | 49.979
2020-03-07 | 1:08 | 49.978
2020-03-07 | 1:08 | 49.977
2020-03-07 | 1:08 | 49.978
2020-03-07 | 1:08 | 49.982
2020-03-07 | 1:08 | 49.985
2020-03-07 | 1:09 | 49.988
2020-03-07 | 1:09 | 49.991
2020-03-07 | 1:09 | 49.995
2020-03-07 | 1:09 | 49.998
2020-03-07 | 1:09 | 50
2020-03-07 | 1:09 | 50.006
2020-03-07 | 1:09 | 50.012
2020-03-07 | 1:09 | 50.017
2020-03-07 | 1:09 | 50.021
2020-03-07 | 1:09 | 50.022
2020-03-07 | 1:09 | 50.025
2020-03-07 | 1:09 | 50.027
2020-03-07 | 1:09 | 50.027
2020-03-07 | 1:09 | 50.027
2020-03-07 | 1:09 | 50.028
2020-03-07 | 1:09 | 50.029
2020-03-07 | 1:09 | 50.029
2020-03-07 | 1:09 | 50.029
2020-03-07 | 1:09 | 50.03
2020-03-07 | 1:09 | 50.03
2020-03-07 | 1:09 | 50.029
2020-03-07 | 1:09 | 50.028
2020-03-07 | 1:09 | 50.028
2020-03-07 | 1:09 | 50.028
2020-03-07 | 1:09 | 50.029
2020-03-07 | 1:09 | 50.027
2020-03-07 | 1:09 | 50.027
2020-03-07 | 1:09 | 50.027
2020-03-07 | 1:09 | 50.027

## Event 20200307-2
In UTC
Date | Time | Freq
2020-03-07 | 4:40 | 50.034
2020-03-07 | 4:40 | 50.033
2020-03-07 | 4:40 | 50.033
2020-03-07 | 4:40 | 50.034
2020-03-07 | 4:40 | 50.033
2020-03-07 | 4:40 | 50.033
2020-03-07 | 4:40 | 50.036
2020-03-07 | 4:40 | 50.035
2020-03-07 | 4:40 | 50.035
2020-03-07 | 4:40 | 50.037
2020-03-07 | 4:40 | 50.037
2020-03-07 | 4:40 | 50.037
2020-03-07 | 4:40 | 50.035
2020-03-07 | 4:40 | 50.036
2020-03-07 | 4:40 | 50.036
2020-03-07 | 4:40 | 50.037
2020-03-07 | 4:40 | 50.037
2020-03-07 | 4:40 | 50.037
2020-03-07 | 4:40 | 50.038
2020-03-07 | 4:40 | 50.037
2020-03-07 | 4:40 | 50.037
2020-03-07 | 4:40 | 50.039
2020-03-07 | 4:40 | 50.039
2020-03-07 | 4:40 | 50.041
2020-03-07 | 4:40 | 50.042
2020-03-07 | 4:40 | 50.043
2020-03-07 | 4:40 | 50.044
2020-03-07 | 4:40 | 50.045
2020-03-07 | 4:40 | 50.047
2020-03-07 | 4:40 | 50.046
2020-03-07 | 4:40 | 50.045
2020-03-07 | 4:41 | 50.044
2020-03-07 | 4:41 | 50.043
2020-03-07 | 4:41 | 50.042
2020-03-07 | 4:41 | 50.04
2020-03-07 | 4:41 | 50.038
2020-03-07 | 4:41 | 50.037
2020-03-07 | 4:41 | 50.036
2020-03-07 | 4:41 | 50.035
2020-03-07 | 4:41 | 50.033
2020-03-07 | 4:41 | 50.031
2020-03-07 | 4:41 | 50.027
2020-03-07 | 4:41 | 50.025
2020-03-07 | 4:41 | 50.023
2020-03-07 | 4:41 | 50.018
2020-03-07 | 4:41 | 50.016
2020-03-07 | 4:41 | 50.014
2020-03-07 | 4:41 | 50.015
2020-03-07 | 4:41 | 50.013
2020-03-07 | 4:41 | 50.013
2020-03-07 | 4:41 | 50.015
2020-03-07 | 4:41 | 50.014
2020-03-07 | 4:41 | 50.014
2020-03-07 | 4:41 | 50.014
2020-03-07 | 4:41 | 50.013
2020-03-07 | 4:41 | 50.013
2020-03-07 | 4:41 | 50.012
2020-03-07 | 4:41 | 50.012
2020-03-07 | 4:41 | 50.012
2020-03-07 | 4:41 | 50.011
2020-03-07 | 4:41 | 50.01
2020-03-07 | 4:41 | 50.008
2020-03-07 | 4:41 | 50.005
2020-03-07 | 4:41 | 50.001
2020-03-07 | 4:41 | 49.996
2020-03-07 | 4:41 | 49.994
2020-03-07 | 4:41 | 49.992
2020-03-07 | 4:41 | 49.991
2020-03-07 | 4:41 | 49.992
2020-03-07 | 4:41 | 49.992
2020-03-07 | 4:41 | 49.994
2020-03-07 | 4:41 | 49.994
2020-03-07 | 4:41 | 49.987
2020-03-07 | 4:41 | 49.976
2020-03-07 | 4:41 | 49.964
2020-03-07 | 4:41 | 49.959
2020-03-07 | 4:41 | 49.955
2020-03-07 | 4:41 | 49.954
2020-03-07 | 4:41 | 49.954
2020-03-07 | 4:41 | 49.956
2020-03-07 | 4:41 | 49.956
2020-03-07 | 4:41 | 49.957
2020-03-07 | 4:41 | 49.958
2020-03-07 | 4:41 | 49.959
2020-03-07 | 4:41 | 49.96
2020-03-07 | 4:41 | 49.96
2020-03-07 | 4:41 | 49.957
2020-03-07 | 4:41 | 49.957
2020-03-07 | 4:41 | 49.955
2020-03-07 | 4:41 | 49.956
2020-03-07 | 4:42 | 49.956
2020-03-07 | 4:42 | 49.955
2020-03-07 | 4:42 | 49.952
2020-03-07 | 4:42 | 49.951
2020-03-07 | 4:42 | 49.948
2020-03-07 | 4:42 | 49.946
2020-03-07 | 4:42 | 49.944
2020-03-07 | 4:42 | 49.944
2020-03-07 | 4:42 | 49.942
2020-03-07 | 4:42 | 49.944
2020-03-07 | 4:42 | 49.945
2020-03-07 | 4:42 | 49.947
2020-03-07 | 4:42 | 49.947
2020-03-07 | 4:42 | 49.948
2020-03-07 | 4:42 | 49.95
2020-03-07 | 4:42 | 49.948
2020-03-07 | 4:42 | 49.948
2020-03-07 | 4:42 | 49.949
2020-03-07 | 4:42 | 49.95
2020-03-07 | 4:42 | 49.953
2020-03-07 | 4:42 | 49.953
2020-03-07 | 4:42 | 49.954
2020-03-07 | 4:42 | 49.955
2020-03-07 | 4:42 | 49.956
2020-03-07 | 4:42 | 49.956
2020-03-07 | 4:42 | 49.956
2020-03-07 | 4:42 | 49.957
2020-03-07 | 4:42 | 49.956
2020-03-07 | 4:42 | 49.955
2020-03-07 | 4:42 | 49.954
2020-03-07 | 4:42 | 49.953
2020-03-07 | 4:42 | 49.952
2020-03-07 | 4:42 | 49.952
2020-03-07 | 4:42 | 49.951
2020-03-07 | 4:42 | 49.951
2020-03-07 | 4:42 | 49.951
2020-03-07 | 4:42 | 49.953
2020-03-07 | 4:42 | 49.955
2020-03-07 | 4:42 | 49.955
2020-03-07 | 4:42 | 49.956
2020-03-07 | 4:42 | 49.957
2020-03-07 | 4:42 | 49.957
2020-03-07 | 4:42 | 49.957
2020-03-07 | 4:42 | 49.957
2020-03-07 | 4:42 | 49.955
2020-03-07 | 4:42 | 49.952
2020-03-07 | 4:42 | 49.952
2020-03-07 | 4:42 | 49.951
2020-03-07 | 4:42 | 49.952
2020-03-07 | 4:42 | 49.951
2020-03-07 | 4:42 | 49.953
2020-03-07 | 4:42 | 49.954
2020-03-07 | 4:42 | 49.954
2020-03-07 | 4:42 | 49.955
2020-03-07 | 4:42 | 49.955
2020-03-07 | 4:42 | 49.954
2020-03-07 | 4:42 | 49.955
2020-03-07 | 4:42 | 49.956
2020-03-07 | 4:42 | 49.957
2020-03-07 | 4:42 | 49.958
2020-03-07 | 4:42 | 49.956
2020-03-07 | 4:43 | 49.956
2020-03-07 | 4:43 | 49.955
2020-03-07 | 4:43 | 49.953
2020-03-07 | 4:43 | 49.952
2020-03-07 | 4:43 | 49.95
2020-03-07 | 4:43 | 49.948
2020-03-07 | 4:43 | 49.947
2020-03-07 | 4:43 | 49.946
2020-03-07 | 4:43 | 49.945
2020-03-07 | 4:43 | 49.946
2020-03-07 | 4:43 | 49.947
2020-03-07 | 4:43 | 49.95
2020-03-07 | 4:43 | 49.952
2020-03-07 | 4:43 | 49.956
2020-03-07 | 4:43 | 49.957
2020-03-07 | 4:43 | 49.958
2020-03-07 | 4:43 | 49.958
2020-03-07 | 4:43 | 49.96
2020-03-07 | 4:43 | 49.959
2020-03-07 | 4:43 | 49.959
2020-03-07 | 4:43 | 49.958
2020-03-07 | 4:43 | 49.958
2020-03-07 | 4:43 | 49.957
2020-03-07 | 4:43 | 49.958
2020-03-07 | 4:43 | 49.958
2020-03-07 | 4:43 | 49.959
2020-03-07 | 4:43 | 49.96
2020-03-07 | 4:43 | 49.96
2020-03-07 | 4:43 | 49.96
2020-03-07 | 4:43 | 49.959
2020-03-07 | 4:43 | 49.957
2020-03-07 | 4:43 | 49.957
2020-03-07 | 4:43 | 49.955
2020-03-07 | 4:43 | 49.956
2020-03-07 | 4:43 | 49.957
2020-03-07 | 4:43 | 49.958
2020-03-07 | 4:43 | 49.959
2020-03-07 | 4:43 | 49.958
2020-03-07 | 4:43 | 49.957
2020-03-07 | 4:43 | 49.958
2020-03-07 | 4:43 | 49.959
2020-03-07 | 4:43 | 49.961
2020-03-07 | 4:43 | 49.965
2020-03-07 | 4:43 | 49.966
2020-03-07 | 4:43 | 49.968
2020-03-07 | 4:43 | 49.971
2020-03-07 | 4:43 | 49.973
2020-03-07 | 4:43 | 49.975
2020-03-07 | 4:43 | 49.976
2020-03-07 | 4:43 | 49.977
2020-03-07 | 4:43 | 49.975
2020-03-07 | 4:43 | 49.974
2020-03-07 | 4:43 | 49.973
2020-03-07 | 4:43 | 49.972
2020-03-07 | 4:43 | 49.971
2020-03-07 | 4:43 | 49.97
2020-03-07 | 4:43 | 49.97
2020-03-07 | 4:43 | 49.969
2020-03-07 | 4:43 | 49.967
2020-03-07 | 4:44 | 49.967
2020-03-07 | 4:44 | 49.967
2020-03-07 | 4:44 | 49.968
2020-03-07 | 4:44 | 49.968
2020-03-07 | 4:44 | 49.97
2020-03-07 | 4:44 | 49.97
2020-03-07 | 4:44 | 49.972
2020-03-07 | 4:44 | 49.972
2020-03-07 | 4:44 | 49.974
2020-03-07 | 4:44 | 49.974
2020-03-07 | 4:44 | 49.974
2020-03-07 | 4:44 | 49.976
2020-03-07 | 4:44 | 49.976
2020-03-07 | 4:44 | 49.978
2020-03-07 | 4:44 | 49.975
2020-03-07 | 4:44 | 49.974
2020-03-07 | 4:44 | 49.973
2020-03-07 | 4:44 | 49.97
2020-03-07 | 4:44 | 49.967
2020-03-07 | 4:44 | 49.966
2020-03-07 | 4:44 | 49.968
2020-03-07 | 4:44 | 49.968
2020-03-07 | 4:44 | 49.969
2020-03-07 | 4:44 | 49.967
2020-03-07 | 4:44 | 49.969
2020-03-07 | 4:44 | 49.97
2020-03-07 | 4:44 | 49.971
2020-03-07 | 4:44 | 49.97
2020-03-07 | 4:44 | 49.971
2020-03-07 | 4:44 | 49.969
2020-03-07 | 4:44 | 49.971
2020-03-07 | 4:44 | 49.968
2020-03-07 | 4:44 | 49.965
2020-03-07 | 4:44 | 49.962
2020-03-07 | 4:44 | 49.961
2020-03-07 | 4:44 | 49.961
2020-03-07 | 4:44 | 49.961
2020-03-07 | 4:44 | 49.959
2020-03-07 | 4:44 | 49.958
2020-03-07 | 4:44 | 49.956
2020-03-07 | 4:44 | 49.956
2020-03-07 | 4:44 | 49.958
2020-03-07 | 4:44 | 49.959
2020-03-07 | 4:44 | 49.959
2020-03-07 | 4:44 | 49.96
2020-03-07 | 4:44 | 49.963
2020-03-07 | 4:44 | 49.965
2020-03-07 | 4:44 | 49.966
2020-03-07 | 4:44 | 49.965
2020-03-07 | 4:44 | 49.966
2020-03-07 | 4:44 | 49.966
2020-03-07 | 4:44 | 49.966
2020-03-07 | 4:44 | 49.967
2020-03-07 | 4:44 | 49.966
2020-03-07 | 4:44 | 49.968
2020-03-07 | 4:44 | 49.967
2020-03-07 | 4:44 | 49.968
2020-03-07 | 4:44 | 49.968
2020-03-07 | 4:44 | 49.966
2020-03-07 | 4:44 | 49.968
2020-03-07 | 4:44 | 49.969
2020-03-07 | 4:45 | 49.968
2020-03-07 | 4:45 | 49.968
2020-03-07 | 4:45 | 49.967
2020-03-07 | 4:45 | 49.967
2020-03-07 | 4:45 | 49.965
2020-03-07 | 4:45 | 49.966
2020-03-07 | 4:45 | 49.967
2020-03-07 | 4:45 | 49.968
2020-03-07 | 4:45 | 49.966
2020-03-07 | 4:45 | 49.966
2020-03-07 | 4:45 | 49.966
2020-03-07 | 4:45 | 49.967
2020-03-07 | 4:45 | 49.966
2020-03-07 | 4:45 | 49.966
2020-03-07 | 4:45 | 49.967
2020-03-07 | 4:45 | 49.968
2020-03-07 | 4:45 | 49.968
2020-03-07 | 4:45 | 49.968
2020-03-07 | 4:45 | 49.97
2020-03-07 | 4:45 | 49.97
2020-03-07 | 4:45 | 49.97
2020-03-07 | 4:45 | 49.97
2020-03-07 | 4:45 | 49.971
2020-03-07 | 4:45 | 49.971
2020-03-07 | 4:45 | 49.973
2020-03-07 | 4:45 | 49.973
2020-03-07 | 4:45 | 49.973
2020-03-07 | 4:45 | 49.974
2020-03-07 | 4:45 | 49.974
2020-03-07 | 4:45 | 49.973
2020-03-07 | 4:45 | 49.971
2020-03-07 | 4:45 | 49.973
2020-03-07 | 4:45 | 49.974
2020-03-07 | 4:45 | 49.974
2020-03-07 | 4:45 | 49.973
2020-03-07 | 4:45 | 49.971
2020-03-07 | 4:45 | 49.97
2020-03-07 | 4:45 | 49.972
2020-03-07 | 4:45 | 49.973
2020-03-07 | 4:45 | 49.974
2020-03-07 | 4:45 | 49.974
2020-03-07 | 4:45 | 49.973
2020-03-07 | 4:45 | 49.972
2020-03-07 | 4:45 | 49.97
2020-03-07 | 4:45 | 49.969
2020-03-07 | 4:45 | 49.968
2020-03-07 | 4:45 | 49.967
2020-03-07 | 4:45 | 49.967
2020-03-07 | 4:45 | 49.969
2020-03-07 | 4:45 | 49.971
2020-03-07 | 4:45 | 49.972
2020-03-07 | 4:45 | 49.976
2020-03-07 | 4:45 | 49.975
2020-03-07 | 4:45 | 49.976
2020-03-07 | 4:45 | 49.975
2020-03-07 | 4:45 | 49.975
2020-03-07 | 4:45 | 49.975
2020-03-07 | 4:45 | 49.976
2020-03-07 | 4:45 | 49.976
2020-03-07 | 4:46 | 49.977
2020-03-07 | 4:46 | 49.977
2020-03-07 | 4:46 | 49.976
2020-03-07 | 4:46 | 49.976
2020-03-07 | 4:46 | 49.975
2020-03-07 | 4:46 | 49.975
2020-03-07 | 4:46 | 49.974
2020-03-07 | 4:46 | 49.974
2020-03-07 | 4:46 | 49.974
2020-03-07 | 4:46 | 49.973
2020-03-07 | 4:46 | 49.973
2020-03-07 | 4:46 | 49.974
2020-03-07 | 4:46 | 49.976
2020-03-07 | 4:46 | 49.98
2020-03-07 | 4:46 | 49.983
2020-03-07 | 4:46 | 49.985
2020-03-07 | 4:46 | 49.986
2020-03-07 | 4:46 | 49.986
2020-03-07 | 4:46 | 49.986
2020-03-07 | 4:46 | 49.987
2020-03-07 | 4:46 | 49.988
2020-03-07 | 4:46 | 49.988
2020-03-07 | 4:46 | 49.986
2020-03-07 | 4:46 | 49.983
2020-03-07 | 4:46 | 49.982
2020-03-07 | 4:46 | 49.98
2020-03-07 | 4:46 | 49.98
2020-03-07 | 4:46 | 49.981
2020-03-07 | 4:46 | 49.981
2020-03-07 | 4:46 | 49.981
2020-03-07 | 4:46 | 49.98
2020-03-07 | 4:46 | 49.978
2020-03-07 | 4:46 | 49.976
2020-03-07 | 4:46 | 49.976
2020-03-07 | 4:46 | 49.976
2020-03-07 | 4:46 | 49.978
2020-03-07 | 4:46 | 49.978
2020-03-07 | 4:46 | 49.978
2020-03-07 | 4:46 | 49.976
2020-03-07 | 4:46 | 49.976
2020-03-07 | 4:46 | 49.976
2020-03-07 | 4:46 | 49.976
2020-03-07 | 4:46 | 49.977
2020-03-07 | 4:46 | 49.977
2020-03-07 | 4:46 | 49.978
2020-03-07 | 4:46 | 49.978
2020-03-07 | 4:46 | 49.979
2020-03-07 | 4:46 | 49.978
2020-03-07 | 4:46 | 49.978
2020-03-07 | 4:46 | 49.977
2020-03-07 | 4:46 | 49.977
2020-03-07 | 4:46 | 49.976
2020-03-07 | 4:46 | 49.976
2020-03-07 | 4:46 | 49.974
2020-03-07 | 4:46 | 49.973
2020-03-07 | 4:46 | 49.972
2020-03-07 | 4:46 | 49.971
2020-03-07 | 4:46 | 49.972
2020-03-07 | 4:46 | 49.974
2020-03-07 | 4:46 | 49.976
2020-03-07 | 4:46 | 49.978
2020-03-07 | 4:47 | 49.978
2020-03-07 | 4:47 | 49.979
2020-03-07 | 4:47 | 49.98
2020-03-07 | 4:47 | 49.982
2020-03-07 | 4:47 | 49.983
2020-03-07 | 4:47 | 49.983
2020-03-07 | 4:47 | 49.984
2020-03-07 | 4:47 | 49.987
2020-03-07 | 4:47 | 49.988
2020-03-07 | 4:47 | 49.987
2020-03-07 | 4:47 | 49.987
2020-03-07 | 4:47 | 49.987
2020-03-07 | 4:47 | 49.986
2020-03-07 | 4:47 | 49.986
2020-03-07 | 4:47 | 49.987
2020-03-07 | 4:47 | 49.988
2020-03-07 | 4:47 | 49.99
2020-03-07 | 4:47 | 49.991
2020-03-07 | 4:47 | 49.992
2020-03-07 | 4:47 | 49.993
2020-03-07 | 4:47 | 49.992
2020-03-07 | 4:47 | 49.99
2020-03-07 | 4:47 | 49.99
2020-03-07 | 4:47 | 49.988
2020-03-07 | 4:47 | 49.989
2020-03-07 | 4:47 | 49.989
2020-03-07 | 4:47 | 49.987
2020-03-07 | 4:47 | 49.987
2020-03-07 | 4:47 | 49.988
2020-03-07 | 4:47 | 49.987
2020-03-07 | 4:47 | 49.984
2020-03-07 | 4:47 | 49.981
2020-03-07 | 4:47 | 49.979
2020-03-07 | 4:47 | 49.978
2020-03-07 | 4:47 | 49.977
2020-03-07 | 4:47 | 49.978
2020-03-07 | 4:47 | 49.98
2020-03-07 | 4:47 | 49.983
2020-03-07 | 4:47 | 49.985
2020-03-07 | 4:47 | 49.985
2020-03-07 | 4:47 | 49.985
2020-03-07 | 4:47 | 49.985
2020-03-07 | 4:47 | 49.985
2020-03-07 | 4:47 | 49.984
2020-03-07 | 4:47 | 49.983
2020-03-07 | 4:47 | 49.981
2020-03-07 | 4:47 | 49.979
2020-03-07 | 4:47 | 49.979
2020-03-07 | 4:47 | 49.98
2020-03-07 | 4:47 | 49.98
2020-03-07 | 4:47 | 49.979
2020-03-07 | 4:47 | 49.98
2020-03-07 | 4:47 | 49.983
2020-03-07 | 4:47 | 49.983
2020-03-07 | 4:47 | 49.982
2020-03-07 | 4:47 | 49.982
2020-03-07 | 4:47 | 49.982
2020-03-07 | 4:47 | 49.982
2020-03-07 | 4:47 | 49.979
2020-03-07 | 4:48 | 49.982
2020-03-07 | 4:48 | 49.982
2020-03-07 | 4:48 | 49.982
2020-03-07 | 4:48 | 49.983
2020-03-07 | 4:48 | 49.983
2020-03-07 | 4:48 | 49.983
2020-03-07 | 4:48 | 49.983
2020-03-07 | 4:48 | 49.984
2020-03-07 | 4:48 | 49.982
2020-03-07 | 4:48 | 49.98
2020-03-07 | 4:48 | 49.979
2020-03-07 | 4:48 | 49.981
2020-03-07 | 4:48 | 49.984
2020-03-07 | 4:48 | 49.986
2020-03-07 | 4:48 | 49.985
2020-03-07 | 4:48 | 49.985
2020-03-07 | 4:48 | 49.986
2020-03-07 | 4:48 | 49.988
2020-03-07 | 4:48 | 49.99
2020-03-07 | 4:48 | 49.989
2020-03-07 | 4:48 | 49.991
2020-03-07 | 4:48 | 49.992
2020-03-07 | 4:48 | 49.991
2020-03-07 | 4:48 | 49.99
2020-03-07 | 4:48 | 49.989
2020-03-07 | 4:48 | 49.989
2020-03-07 | 4:48 | 49.989
2020-03-07 | 4:48 | 49.99
2020-03-07 | 4:48 | 49.99
2020-03-07 | 4:48 | 49.992
2020-03-07 | 4:48 | 49.994
2020-03-07 | 4:48 | 49.994
2020-03-07 | 4:48 | 49.994
2020-03-07 | 4:48 | 49.994
2020-03-07 | 4:48 | 49.995
2020-03-07 | 4:48 | 49.996
2020-03-07 | 4:48 | 49.997
2020-03-07 | 4:48 | 49.999
2020-03-07 | 4:48 | 50
2020-03-07 | 4:48 | 50.003
2020-03-07 | 4:48 | 50.005
2020-03-07 | 4:48 | 50.006
2020-03-07 | 4:48 | 50.007
2020-03-07 | 4:48 | 50.008
2020-03-07 | 4:48 | 50.006
2020-03-07 | 4:48 | 50.006
2020-03-07 | 4:48 | 50.005
2020-03-07 | 4:48 | 50.005
2020-03-07 | 4:48 | 50.004
2020-03-07 | 4:48 | 50.002
2020-03-07 | 4:48 | 49.999
2020-03-07 | 4:48 | 49.998
2020-03-07 | 4:48 | 49.997
2020-03-07 | 4:48 | 49.998
2020-03-07 | 4:48 | 49.999
2020-03-07 | 4:48 | 49.999
2020-03-07 | 4:48 | 50
2020-03-07 | 4:48 | 50.001
2020-03-07 | 4:48 | 50.002
2020-03-07 | 4:48 | 50.003
2020-03-07 | 4:48 | 50.007
2020-03-07 | 4:49 | 50.007
2020-03-07 | 4:49 | 50.008
2020-03-07 | 4:49 | 50.006
2020-03-07 | 4:49 | 50.005
2020-03-07 | 4:49 | 50.005
2020-03-07 | 4:49 | 50.004
2020-03-07 | 4:49 | 50.006
2020-03-07 | 4:49 | 50.008
2020-03-07 | 4:49 | 50.013
2020-03-07 | 4:49 | 50.019
2020-03-07 | 4:49 | 50.023
2020-03-07 | 4:49 | 50.026
2020-03-07 | 4:49 | 50.028
2020-03-07 | 4:49 | 50.031
2020-03-07 | 4:49 | 50.03
2020-03-07 | 4:49 | 50.03
2020-03-07 | 4:49 | 50.028
2020-03-07 | 4:49 | 50.028
2020-03-07 | 4:49 | 50.028
2020-03-07 | 4:49 | 50.028
2020-03-07 | 4:49 | 50.029
2020-03-07 | 4:49 | 50.029
2020-03-07 | 4:49 | 50.031
2020-03-07 | 4:49 | 50.031
2020-03-07 | 4:49 | 50.032
2020-03-07 | 4:49 | 50.031
2020-03-07 | 4:49 | 50.031
2020-03-07 | 4:49 | 50.03
2020-03-07 | 4:49 | 50.028

## Event 20200318-1
In UTC
Date | Time | Freq
2020-03-18 | 15:09 | 49.933
2020-03-18 | 15:09 | 49.933
2020-03-18 | 15:09 | 49.936
2020-03-18 | 15:09 | 49.937
2020-03-18 | 15:09 | 49.939
2020-03-18 | 15:09 | 49.94
2020-03-18 | 15:09 | 49.94
2020-03-18 | 15:09 | 49.94
2020-03-18 | 15:09 | 49.938
2020-03-18 | 15:09 | 49.94
2020-03-18 | 15:09 | 49.939
2020-03-18 | 15:09 | 49.939
2020-03-18 | 15:09 | 49.944
2020-03-18 | 15:09 | 49.944
2020-03-18 | 15:09 | 49.946
2020-03-18 | 15:09 | 49.945
2020-03-18 | 15:09 | 49.946
2020-03-18 | 15:09 | 49.945
2020-03-18 | 15:09 | 49.947
2020-03-18 | 15:09 | 49.947
2020-03-18 | 15:09 | 49.947
2020-03-18 | 15:09 | 49.947
2020-03-18 | 15:09 | 49.948
2020-03-18 | 15:09 | 49.949
2020-03-18 | 15:09 | 49.949
2020-03-18 | 15:09 | 49.95
2020-03-18 | 15:09 | 49.951
2020-03-18 | 15:09 | 49.954
2020-03-18 | 15:09 | 49.954
2020-03-18 | 15:09 | 49.956
2020-03-18 | 15:10 | 49.957
2020-03-18 | 15:10 | 49.958
2020-03-18 | 15:10 | 49.957
2020-03-18 | 15:10 | 49.959
2020-03-18 | 15:10 | 49.958
2020-03-18 | 15:10 | 49.957
2020-03-18 | 15:10 | 49.96
2020-03-18 | 15:10 | 49.96
2020-03-18 | 15:10 | 49.961
2020-03-18 | 15:10 | 49.958
2020-03-18 | 15:10 | 49.956
2020-03-18 | 15:10 | 49.954
2020-03-18 | 15:10 | 49.955
2020-03-18 | 15:10 | 49.954
2020-03-18 | 15:10 | 49.955
2020-03-18 | 15:10 | 49.954
2020-03-18 | 15:10 | 49.957
2020-03-18 | 15:10 | 49.96
2020-03-18 | 15:10 | 49.963
2020-03-18 | 15:10 | 49.965
2020-03-18 | 15:10 | 49.966
2020-03-18 | 15:10 | 49.966
2020-03-18 | 15:10 | 49.966
2020-03-18 | 15:10 | 49.966
2020-03-18 | 15:10 | 49.965
2020-03-18 | 15:10 | 49.961
2020-03-18 | 15:10 | 49.96
2020-03-18 | 15:10 | 49.956
2020-03-18 | 15:10 | 49.955
2020-03-18 | 15:10 | 49.953
2020-03-18 | 15:10 | 49.95
2020-03-18 | 15:10 | 49.945
2020-03-18 | 15:10 | 49.941
2020-03-18 | 15:10 | 49.936
2020-03-18 | 15:10 | 49.933
2020-03-18 | 15:10 | 49.931
2020-03-18 | 15:10 | 49.928
2020-03-18 | 15:10 | 49.927
2020-03-18 | 15:10 | 49.924
2020-03-18 | 15:10 | 49.924
2020-03-18 | 15:10 | 49.926
2020-03-18 | 15:10 | 49.928
2020-03-18 | 15:10 | 49.927
2020-03-18 | 15:10 | 49.929
2020-03-18 | 15:10 | 49.929
2020-03-18 | 15:10 | 49.929
2020-03-18 | 15:10 | 49.93
2020-03-18 | 15:10 | 49.929
2020-03-18 | 15:10 | 49.932
2020-03-18 | 15:10 | 49.933
2020-03-18 | 15:10 | 49.932
2020-03-18 | 15:10 | 49.936
2020-03-18 | 15:10 | 49.94
2020-03-18 | 15:10 | 49.942
2020-03-18 | 15:10 | 49.944
2020-03-18 | 15:10 | 49.945
2020-03-18 | 15:10 | 49.943
2020-03-18 | 15:10 | 49.944
2020-03-18 | 15:10 | 49.944
2020-03-18 | 15:10 | 49.94
2020-03-18 | 15:10 | 49.94
2020-03-18 | 15:11 | 49.939
2020-03-18 | 15:11 | 49.938
2020-03-18 | 15:11 | 49.939
2020-03-18 | 15:11 | 49.937
2020-03-18 | 15:11 | 49.935
2020-03-18 | 15:11 | 49.933
2020-03-18 | 15:11 | 49.93
2020-03-18 | 15:11 | 49.925
2020-03-18 | 15:11 | 49.922
2020-03-18 | 15:11 | 49.922
2020-03-18 | 15:11 | 49.918
2020-03-18 | 15:11 | 49.916
2020-03-18 | 15:11 | 49.91
2020-03-18 | 15:11 | 49.907
2020-03-18 | 15:11 | 49.88
2020-03-18 | 15:11 | 49.85
2020-03-18 | 15:11 | 49.832
2020-03-18 | 15:11 | 49.817
2020-03-18 | 15:11 | 49.811
2020-03-18 | 15:11 | 49.806
2020-03-18 | 15:11 | 49.802
2020-03-18 | 15:11 | 49.801
2020-03-18 | 15:11 | 49.798
2020-03-18 | 15:11 | 49.799
2020-03-18 | 15:11 | 49.799
2020-03-18 | 15:11 | 49.798
2020-03-18 | 15:11 | 49.797
2020-03-18 | 15:11 | 49.797
2020-03-18 | 15:11 | 49.795
2020-03-18 | 15:11 | 49.796
2020-03-18 | 15:11 | 49.796
2020-03-18 | 15:11 | 49.797
2020-03-18 | 15:11 | 49.798
2020-03-18 | 15:11 | 49.799
2020-03-18 | 15:11 | 49.8
2020-03-18 | 15:11 | 49.802
2020-03-18 | 15:11 | 49.804
2020-03-18 | 15:11 | 49.807
2020-03-18 | 15:11 | 49.808
2020-03-18 | 15:11 | 49.812
2020-03-18 | 15:11 | 49.814
2020-03-18 | 15:11 | 49.819
2020-03-18 | 15:11 | 49.822
2020-03-18 | 15:11 | 49.827
2020-03-18 | 15:11 | 49.829
2020-03-18 | 15:11 | 49.831
2020-03-18 | 15:11 | 49.832
2020-03-18 | 15:11 | 49.833
2020-03-18 | 15:11 | 49.833
2020-03-18 | 15:11 | 49.833
2020-03-18 | 15:11 | 49.834
2020-03-18 | 15:11 | 49.835
2020-03-18 | 15:11 | 49.838
2020-03-18 | 15:11 | 49.839
2020-03-18 | 15:11 | 49.84
2020-03-18 | 15:11 | 49.84
2020-03-18 | 15:11 | 49.84
2020-03-18 | 15:11 | 49.841
2020-03-18 | 15:11 | 49.844
2020-03-18 | 15:12 | 49.842
2020-03-18 | 15:12 | 49.844
2020-03-18 | 15:12 | 49.847
2020-03-18 | 15:12 | 49.846
2020-03-18 | 15:12 | 49.847
2020-03-18 | 15:12 | 49.847
2020-03-18 | 15:12 | 49.844
2020-03-18 | 15:12 | 49.843
2020-03-18 | 15:12 | 49.842
2020-03-18 | 15:12 | 49.839
2020-03-18 | 15:12 | 49.837
2020-03-18 | 15:12 | 49.837
2020-03-18 | 15:12 | 49.836
2020-03-18 | 15:12 | 49.836
2020-03-18 | 15:12 | 49.836
2020-03-18 | 15:12 | 49.836
2020-03-18 | 15:12 | 49.836
2020-03-18 | 15:12 | 49.837
2020-03-18 | 15:12 | 49.836
2020-03-18 | 15:12 | 49.834
2020-03-18 | 15:12 | 49.834
2020-03-18 | 15:12 | 49.832
2020-03-18 | 15:12 | 49.83
2020-03-18 | 15:12 | 49.831
2020-03-18 | 15:12 | 49.836
2020-03-18 | 15:12 | 49.841
2020-03-18 | 15:12 | 49.844
2020-03-18 | 15:12 | 49.849
2020-03-18 | 15:12 | 49.849
2020-03-18 | 15:12 | 49.848
2020-03-18 | 15:12 | 49.847
2020-03-18 | 15:12 | 49.848
2020-03-18 | 15:12 | 49.848
2020-03-18 | 15:12 | 49.847
2020-03-18 | 15:12 | 49.849
2020-03-18 | 15:12 | 49.85
2020-03-18 | 15:12 | 49.851
2020-03-18 | 15:12 | 49.854
2020-03-18 | 15:12 | 49.857
2020-03-18 | 15:12 | 49.859
2020-03-18 | 15:12 | 49.862
2020-03-18 | 15:12 | 49.864
2020-03-18 | 15:12 | 49.869
2020-03-18 | 15:12 | 49.875
2020-03-18 | 15:12 | 49.883
2020-03-18 | 15:12 | 49.887
2020-03-18 | 15:12 | 49.892
2020-03-18 | 15:12 | 49.896
2020-03-18 | 15:12 | 49.9
2020-03-18 | 15:12 | 49.903
2020-03-18 | 15:12 | 49.906
2020-03-18 | 15:12 | 49.914
2020-03-18 | 15:12 | 49.922
2020-03-18 | 15:12 | 49.927
2020-03-18 | 15:12 | 49.932
2020-03-18 | 15:12 | 49.935
2020-03-18 | 15:12 | 49.936
2020-03-18 | 15:12 | 49.937
2020-03-18 | 15:12 | 49.938
2020-03-18 | 15:12 | 49.939
2020-03-18 | 15:12 | 49.94
2020-03-18 | 15:13 | 49.941
2020-03-18 | 15:13 | 49.945
2020-03-18 | 15:13 | 49.945
2020-03-18 | 15:13 | 49.946
2020-03-18 | 15:13 | 49.947
2020-03-18 | 15:13 | 49.949
2020-03-18 | 15:13 | 49.952
2020-03-18 | 15:13 | 49.956
2020-03-18 | 15:13 | 49.959
2020-03-18 | 15:13 | 49.961
2020-03-18 | 15:13 | 49.963
2020-03-18 | 15:13 | 49.963
2020-03-18 | 15:13 | 49.963
2020-03-18 | 15:13 | 49.963
2020-03-18 | 15:13 | 49.961
2020-03-18 | 15:13 | 49.958
2020-03-18 | 15:13 | 49.953
2020-03-18 | 15:13 | 49.949
2020-03-18 | 15:13 | 49.946
2020-03-18 | 15:13 | 49.946
2020-03-18 | 15:13 | 49.943
2020-03-18 | 15:13 | 49.939
2020-03-18 | 15:13 | 49.938
2020-03-18 | 15:13 | 49.939
2020-03-18 | 15:13 | 49.937
2020-03-18 | 15:13 | 49.937
2020-03-18 | 15:13 | 49.937
2020-03-18 | 15:13 | 49.938
2020-03-18 | 15:13 | 49.938
2020-03-18 | 15:13 | 49.938
2020-03-18 | 15:13 | 49.939
2020-03-18 | 15:13 | 49.94
2020-03-18 | 15:13 | 49.942
2020-03-18 | 15:13 | 49.942
2020-03-18 | 15:13 | 49.944
2020-03-18 | 15:13 | 49.947
2020-03-18 | 15:13 | 49.949
2020-03-18 | 15:13 | 49.951
2020-03-18 | 15:13 | 49.956
2020-03-18 | 15:13 | 49.958
2020-03-18 | 15:13 | 49.96
2020-03-18 | 15:13 | 49.962
2020-03-18 | 15:13 | 49.96
2020-03-18 | 15:13 | 49.959
2020-03-18 | 15:13 | 49.961
2020-03-18 | 15:13 | 49.962
2020-03-18 | 15:13 | 49.963
2020-03-18 | 15:13 | 49.964
2020-03-18 | 15:13 | 49.963
2020-03-18 | 15:13 | 49.96
2020-03-18 | 15:13 | 49.96
2020-03-18 | 15:13 | 49.958
2020-03-18 | 15:13 | 49.958
2020-03-18 | 15:13 | 49.96
2020-03-18 | 15:13 | 49.96
2020-03-18 | 15:13 | 49.958
2020-03-18 | 15:13 | 49.96
2020-03-18 | 15:13 | 49.961
2020-03-18 | 15:13 | 49.962
2020-03-18 | 15:14 | 49.964
2020-03-18 | 15:14 | 49.966
2020-03-18 | 15:14 | 49.968
2020-03-18 | 15:14 | 49.969
2020-03-18 | 15:14 | 49.97
2020-03-18 | 15:14 | 49.972
2020-03-18 | 15:14 | 49.972
2020-03-18 | 15:14 | 49.973
2020-03-18 | 15:14 | 49.974
2020-03-18 | 15:14 | 49.976
2020-03-18 | 15:14 | 49.975
2020-03-18 | 15:14 | 49.976
2020-03-18 | 15:14 | 49.974
2020-03-18 | 15:14 | 49.973
2020-03-18 | 15:14 | 49.968
2020-03-18 | 15:14 | 49.964
2020-03-18 | 15:14 | 49.96
2020-03-18 | 15:14 | 49.958
2020-03-18 | 15:14 | 49.956
2020-03-18 | 15:14 | 49.952
2020-03-18 | 15:14 | 49.953
2020-03-18 | 15:14 | 49.953
2020-03-18 | 15:14 | 49.951
2020-03-18 | 15:14 | 49.95
2020-03-18 | 15:14 | 49.948
2020-03-18 | 15:14 | 49.949
2020-03-18 | 15:14 | 49.947
2020-03-18 | 15:14 | 49.949
2020-03-18 | 15:14 | 49.947
2020-03-18 | 15:14 | 49.946
2020-03-18 | 15:14 | 49.944
2020-03-18 | 15:14 | 49.943
2020-03-18 | 15:14 | 49.941
2020-03-18 | 15:14 | 49.94
2020-03-18 | 15:14 | 49.939
2020-03-18 | 15:14 | 49.936
2020-03-18 | 15:14 | 49.934
2020-03-18 | 15:14 | 49.935
2020-03-18 | 15:14 | 49.934
2020-03-18 | 15:14 | 49.937
2020-03-18 | 15:14 | 49.937
2020-03-18 | 15:14 | 49.935
2020-03-18 | 15:14 | 49.936
2020-03-18 | 15:14 | 49.935
2020-03-18 | 15:14 | 49.938
2020-03-18 | 15:14 | 49.936
2020-03-18 | 15:14 | 49.937
2020-03-18 | 15:14 | 49.938
2020-03-18 | 15:14 | 49.938
2020-03-18 | 15:14 | 49.94
2020-03-18 | 15:14 | 49.943
2020-03-18 | 15:14 | 49.943
2020-03-18 | 15:14 | 49.945
2020-03-18 | 15:14 | 49.948
2020-03-18 | 15:14 | 49.949
2020-03-18 | 15:14 | 49.953
2020-03-18 | 15:14 | 49.955
2020-03-18 | 15:14 | 49.952
2020-03-18 | 15:14 | 49.949
2020-03-18 | 15:14 | 49.943
2020-03-18 | 15:14 | 49.934
2020-03-18 | 15:15 | 49.93
2020-03-18 | 15:15 | 49.925
2020-03-18 | 15:15 | 49.923
2020-03-18 | 15:15 | 49.922
2020-03-18 | 15:15 | 49.922
2020-03-18 | 15:15 | 49.925
2020-03-18 | 15:15 | 49.924
2020-03-18 | 15:15 | 49.925
2020-03-18 | 15:15 | 49.924
2020-03-18 | 15:15 | 49.923
2020-03-18 | 15:15 | 49.923
2020-03-18 | 15:15 | 49.925
2020-03-18 | 15:15 | 49.927
2020-03-18 | 15:15 | 49.928
2020-03-18 | 15:15 | 49.931
2020-03-18 | 15:15 | 49.931
2020-03-18 | 15:15 | 49.936
2020-03-18 | 15:15 | 49.936
2020-03-18 | 15:15 | 49.94
2020-03-18 | 15:15 | 49.94
2020-03-18 | 15:15 | 49.942
2020-03-18 | 15:15 | 49.944
2020-03-18 | 15:15 | 49.945
2020-03-18 | 15:15 | 49.949
2020-03-18 | 15:15 | 49.949
2020-03-18 | 15:15 | 49.951
2020-03-18 | 15:15 | 49.952
2020-03-18 | 15:15 | 49.953
2020-03-18 | 15:15 | 49.954
2020-03-18 | 15:15 | 49.952
2020-03-18 | 15:15 | 49.953
2020-03-18 | 15:15 | 49.952
2020-03-18 | 15:15 | 49.949
2020-03-18 | 15:15 | 49.951
2020-03-18 | 15:15 | 49.95
2020-03-18 | 15:15 | 49.948
2020-03-18 | 15:15 | 49.948
2020-03-18 | 15:15 | 49.946
2020-03-18 | 15:15 | 49.945
2020-03-18 | 15:15 | 49.948
2020-03-18 | 15:15 | 49.953
2020-03-18 | 15:15 | 49.956
2020-03-18 | 15:15 | 49.961
2020-03-18 | 15:15 | 49.964
2020-03-18 | 15:15 | 49.968
2020-03-18 | 15:15 | 49.971
2020-03-18 | 15:15 | 49.972
2020-03-18 | 15:15 | 49.976
2020-03-18 | 15:15 | 49.977
2020-03-18 | 15:15 | 49.981
2020-03-18 | 15:15 | 49.98
2020-03-18 | 15:15 | 49.981
2020-03-18 | 15:15 | 49.983
2020-03-18 | 15:15 | 49.983
2020-03-18 | 15:15 | 49.983
2020-03-18 | 15:15 | 49.984
2020-03-18 | 15:15 | 49.985
2020-03-18 | 15:15 | 49.984
2020-03-18 | 15:15 | 49.987
2020-03-18 | 15:16 | 49.989
2020-03-18 | 15:16 | 49.991
2020-03-18 | 15:16 | 49.992
2020-03-18 | 15:16 | 49.993
2020-03-18 | 15:16 | 49.991
2020-03-18 | 15:16 | 49.993
2020-03-18 | 15:16 | 49.99
2020-03-18 | 15:16 | 49.987
2020-03-18 | 15:16 | 49.986
2020-03-18 | 15:16 | 49.985
2020-03-18 | 15:16 | 49.984
2020-03-18 | 15:16 | 49.986
2020-03-18 | 15:16 | 49.988
2020-03-18 | 15:16 | 49.989
2020-03-18 | 15:16 | 49.991
2020-03-18 | 15:16 | 49.992
2020-03-18 | 15:16 | 49.992
2020-03-18 | 15:16 | 49.993
2020-03-18 | 15:16 | 49.993
2020-03-18 | 15:16 | 49.989
2020-03-18 | 15:16 | 49.985
2020-03-18 | 15:16 | 49.981
2020-03-18 | 15:16 | 49.979
2020-03-18 | 15:16 | 49.976
2020-03-18 | 15:16 | 49.975
2020-03-18 | 15:16 | 49.972
2020-03-18 | 15:16 | 49.974
2020-03-18 | 15:16 | 49.975
2020-03-18 | 15:16 | 49.976
2020-03-18 | 15:16 | 49.979
2020-03-18 | 15:16 | 49.976
2020-03-18 | 15:16 | 49.976
2020-03-18 | 15:16 | 49.975
2020-03-18 | 15:16 | 49.973
2020-03-18 | 15:16 | 49.974
2020-03-18 | 15:16 | 49.972
2020-03-18 | 15:16 | 49.972
2020-03-18 | 15:16 | 49.971
2020-03-18 | 15:16 | 49.972
2020-03-18 | 15:16 | 49.972
2020-03-18 | 15:16 | 49.973
2020-03-18 | 15:16 | 49.976
2020-03-18 | 15:16 | 49.975
2020-03-18 | 15:16 | 49.977
2020-03-18 | 15:16 | 49.976
2020-03-18 | 15:16 | 49.978
2020-03-18 | 15:16 | 49.976
2020-03-18 | 15:16 | 49.974
2020-03-18 | 15:16 | 49.972
2020-03-18 | 15:16 | 49.97
2020-03-18 | 15:16 | 49.969
2020-03-18 | 15:16 | 49.967
2020-03-18 | 15:16 | 49.967
2020-03-18 | 15:16 | 49.964
2020-03-18 | 15:16 | 49.965
2020-03-18 | 15:16 | 49.965
2020-03-18 | 15:16 | 49.969
2020-03-18 | 15:16 | 49.968
2020-03-18 | 15:16 | 49.97
2020-03-18 | 15:16 | 49.969
2020-03-18 | 15:16 | 49.971
2020-03-18 | 15:17 | 49.973
2020-03-18 | 15:17 | 49.976
2020-03-18 | 15:17 | 49.982
2020-03-18 | 15:17 | 49.985
2020-03-18 | 15:17 | 49.991
2020-03-18 | 15:17 | 49.996
2020-03-18 | 15:17 | 49.998
2020-03-18 | 15:17 | 50.004
2020-03-18 | 15:17 | 50.005
2020-03-18 | 15:17 | 50.007
2020-03-18 | 15:17 | 50.011
2020-03-18 | 15:17 | 50.011
2020-03-18 | 15:17 | 50.011
2020-03-18 | 15:17 | 50.013
2020-03-18 | 15:17 | 50.014
2020-03-18 | 15:17 | 50.017
2020-03-18 | 15:17 | 50.018
2020-03-18 | 15:17 | 50.023
2020-03-18 | 15:17 | 50.025
2020-03-18 | 15:17 | 50.027
2020-03-18 | 15:17 | 50.029
2020-03-18 | 15:17 | 50.031
2020-03-18 | 15:17 | 50.034
2020-03-18 | 15:17 | 50.035
2020-03-18 | 15:17 | 50.034
2020-03-18 | 15:17 | 50.034
2020-03-18 | 15:17 | 50.035
2020-03-18 | 15:17 | 50.037
2020-03-18 | 15:17 | 50.038

## Event 20200320-1
In UTC
Date | Time | Freq
2020-03-20 | 21:00 | 49.898
2020-03-20 | 21:00 | 49.896
2020-03-20 | 21:00 | 49.894
2020-03-20 | 21:00 | 49.894
2020-03-20 | 21:00 | 49.893
2020-03-20 | 21:00 | 49.892
2020-03-20 | 21:00 | 49.891
2020-03-20 | 21:00 | 49.89
2020-03-20 | 21:00 | 49.887
2020-03-20 | 21:00 | 49.885
2020-03-20 | 21:00 | 49.882
2020-03-20 | 21:00 | 49.879
2020-03-20 | 21:00 | 49.875
2020-03-20 | 21:00 | 49.873
2020-03-20 | 21:00 | 49.87
2020-03-20 | 21:00 | 49.869
2020-03-20 | 21:00 | 49.867
2020-03-20 | 21:00 | 49.864
2020-03-20 | 21:00 | 49.862
2020-03-20 | 21:00 | 49.86
2020-03-20 | 21:00 | 49.86
2020-03-20 | 21:00 | 49.859
2020-03-20 | 21:00 | 49.859
2020-03-20 | 21:00 | 49.859
2020-03-20 | 21:00 | 49.86
2020-03-20 | 21:00 | 49.862
2020-03-20 | 21:00 | 49.859
2020-03-20 | 21:00 | 49.862
2020-03-20 | 21:00 | 49.861
2020-03-20 | 21:00 | 49.862
2020-03-20 | 21:00 | 49.864
2020-03-20 | 21:01 | 49.862
2020-03-20 | 21:01 | 49.86
2020-03-20 | 21:01 | 49.859
2020-03-20 | 21:01 | 49.855
2020-03-20 | 21:01 | 49.853
2020-03-20 | 21:01 | 49.851
2020-03-20 | 21:01 | 49.849
2020-03-20 | 21:01 | 49.847
2020-03-20 | 21:01 | 49.845
2020-03-20 | 21:01 | 49.843
2020-03-20 | 21:01 | 49.843
2020-03-20 | 21:01 | 49.842
2020-03-20 | 21:01 | 49.84
2020-03-20 | 21:01 | 49.839
2020-03-20 | 21:01 | 49.84
2020-03-20 | 21:01 | 49.841
2020-03-20 | 21:01 | 49.846
2020-03-20 | 21:01 | 49.846
2020-03-20 | 21:01 | 49.846
2020-03-20 | 21:01 | 49.844
2020-03-20 | 21:01 | 49.84
2020-03-20 | 21:01 | 49.839
2020-03-20 | 21:01 | 49.838
2020-03-20 | 21:01 | 49.835
2020-03-20 | 21:01 | 49.83
2020-03-20 | 21:01 | 49.827
2020-03-20 | 21:01 | 49.823
2020-03-20 | 21:01 | 49.823
2020-03-20 | 21:01 | 49.821
2020-03-20 | 21:01 | 49.816
2020-03-20 | 21:01 | 49.812
2020-03-20 | 21:01 | 49.809
2020-03-20 | 21:01 | 49.808
2020-03-20 | 21:01 | 49.809
2020-03-20 | 21:01 | 49.812
2020-03-20 | 21:01 | 49.817
2020-03-20 | 21:01 | 49.822
2020-03-20 | 21:01 | 49.827
2020-03-20 | 21:01 | 49.834
2020-03-20 | 21:01 | 49.842
2020-03-20 | 21:01 | 49.851
2020-03-20 | 21:01 | 49.859
2020-03-20 | 21:01 | 49.865
2020-03-20 | 21:01 | 49.867
2020-03-20 | 21:01 | 49.868
2020-03-20 | 21:01 | 49.867
2020-03-20 | 21:01 | 49.866
2020-03-20 | 21:01 | 49.863
2020-03-20 | 21:01 | 49.866
2020-03-20 | 21:01 | 49.865
2020-03-20 | 21:01 | 49.864
2020-03-20 | 21:01 | 49.868
2020-03-20 | 21:01 | 49.867
2020-03-20 | 21:01 | 49.868
2020-03-20 | 21:01 | 49.869
2020-03-20 | 21:01 | 49.869
2020-03-20 | 21:01 | 49.869
2020-03-20 | 21:01 | 49.869
2020-03-20 | 21:01 | 49.867
2020-03-20 | 21:02 | 49.869
2020-03-20 | 21:02 | 49.868
2020-03-20 | 21:02 | 49.868
2020-03-20 | 21:02 | 49.869
2020-03-20 | 21:02 | 49.868
2020-03-20 | 21:02 | 49.87
2020-03-20 | 21:02 | 49.871
2020-03-20 | 21:02 | 49.873
2020-03-20 | 21:02 | 49.873
2020-03-20 | 21:02 | 49.875
2020-03-20 | 21:02 | 49.876
2020-03-20 | 21:02 | 49.879
2020-03-20 | 21:02 | 49.882
2020-03-20 | 21:02 | 49.885
2020-03-20 | 21:02 | 49.889
2020-03-20 | 21:02 | 49.894
2020-03-20 | 21:02 | 49.901
2020-03-20 | 21:02 | 49.905
2020-03-20 | 21:02 | 49.908
2020-03-20 | 21:02 | 49.909
2020-03-20 | 21:02 | 49.911
2020-03-20 | 21:02 | 49.912
2020-03-20 | 21:02 | 49.916
2020-03-20 | 21:02 | 49.917
2020-03-20 | 21:02 | 49.916
2020-03-20 | 21:02 | 49.913
2020-03-20 | 21:02 | 49.91
2020-03-20 | 21:02 | 49.909
2020-03-20 | 21:02 | 49.907
2020-03-20 | 21:02 | 49.904
2020-03-20 | 21:02 | 49.905
2020-03-20 | 21:02 | 49.906
2020-03-20 | 21:02 | 49.905
2020-03-20 | 21:02 | 49.902
2020-03-20 | 21:02 | 49.899
2020-03-20 | 21:02 | 49.896
2020-03-20 | 21:02 | 49.892
2020-03-20 | 21:02 | 49.887
2020-03-20 | 21:02 | 49.882
2020-03-20 | 21:02 | 49.88
2020-03-20 | 21:02 | 49.88
2020-03-20 | 21:02 | 49.881
2020-03-20 | 21:02 | 49.882
2020-03-20 | 21:02 | 49.886
2020-03-20 | 21:02 | 49.89
2020-03-20 | 21:02 | 49.893
2020-03-20 | 21:02 | 49.892
2020-03-20 | 21:02 | 49.894
2020-03-20 | 21:02 | 49.897
2020-03-20 | 21:02 | 49.901
2020-03-20 | 21:02 | 49.903
2020-03-20 | 21:02 | 49.905
2020-03-20 | 21:02 | 49.907
2020-03-20 | 21:02 | 49.906
2020-03-20 | 21:02 | 49.906
2020-03-20 | 21:02 | 49.906
2020-03-20 | 21:02 | 49.908
2020-03-20 | 21:02 | 49.909
2020-03-20 | 21:02 | 49.91
2020-03-20 | 21:02 | 49.909
2020-03-20 | 21:02 | 49.911
2020-03-20 | 21:03 | 49.911
2020-03-20 | 21:03 | 49.911
2020-03-20 | 21:03 | 49.911
2020-03-20 | 21:03 | 49.909
2020-03-20 | 21:03 | 49.909
2020-03-20 | 21:03 | 49.908
2020-03-20 | 21:03 | 49.909
2020-03-20 | 21:03 | 49.909
2020-03-20 | 21:03 | 49.907
2020-03-20 | 21:03 | 49.906
2020-03-20 | 21:03 | 49.906
2020-03-20 | 21:03 | 49.908
2020-03-20 | 21:03 | 49.912
2020-03-20 | 21:03 | 49.917
2020-03-20 | 21:03 | 49.921
2020-03-20 | 21:03 | 49.924
2020-03-20 | 21:03 | 49.929
2020-03-20 | 21:03 | 49.931
2020-03-20 | 21:03 | 49.932
2020-03-20 | 21:03 | 49.931
2020-03-20 | 21:03 | 49.929
2020-03-20 | 21:03 | 49.926
2020-03-20 | 21:03 | 49.926
2020-03-20 | 21:03 | 49.928
2020-03-20 | 21:03 | 49.929
2020-03-20 | 21:03 | 49.926
2020-03-20 | 21:03 | 49.926
2020-03-20 | 21:03 | 49.927
2020-03-20 | 21:03 | 49.928
2020-03-20 | 21:03 | 49.93
2020-03-20 | 21:03 | 49.93
2020-03-20 | 21:03 | 49.928
2020-03-20 | 21:03 | 49.922
2020-03-20 | 21:03 | 49.917
2020-03-20 | 21:03 | 49.91
2020-03-20 | 21:03 | 49.901
2020-03-20 | 21:03 | 49.894
2020-03-20 | 21:03 | 49.886
2020-03-20 | 21:03 | 49.877
2020-03-20 | 21:03 | 49.869
2020-03-20 | 21:03 | 49.863
2020-03-20 | 21:03 | 49.861
2020-03-20 | 21:03 | 49.867
2020-03-20 | 21:03 | 49.871
2020-03-20 | 21:03 | 49.882
2020-03-20 | 21:03 | 49.892
2020-03-20 | 21:03 | 49.906
2020-03-20 | 21:03 | 49.92
2020-03-20 | 21:03 | 49.934
2020-03-20 | 21:03 | 49.945
2020-03-20 | 21:03 | 49.948
2020-03-20 | 21:03 | 49.946
2020-03-20 | 21:03 | 49.944
2020-03-20 | 21:03 | 49.942
2020-03-20 | 21:03 | 49.94
2020-03-20 | 21:03 | 49.936
2020-03-20 | 21:03 | 49.934
2020-03-20 | 21:03 | 49.931
2020-03-20 | 21:03 | 49.928
2020-03-20 | 21:04 | 49.925
2020-03-20 | 21:04 | 49.922
2020-03-20 | 21:04 | 49.917
2020-03-20 | 21:04 | 49.922
2020-03-20 | 21:04 | 49.926
2020-03-20 | 21:04 | 49.931
2020-03-20 | 21:04 | 49.936
2020-03-20 | 21:04 | 49.941
2020-03-20 | 21:04 | 49.945
2020-03-20 | 21:04 | 49.948
2020-03-20 | 21:04 | 49.952
2020-03-20 | 21:04 | 49.954
2020-03-20 | 21:04 | 49.955
2020-03-20 | 21:04 | 49.954
2020-03-20 | 21:04 | 49.953
2020-03-20 | 21:04 | 49.953
2020-03-20 | 21:04 | 49.953
2020-03-20 | 21:04 | 49.955
2020-03-20 | 21:04 | 49.954
2020-03-20 | 21:04 | 49.954
2020-03-20 | 21:04 | 49.954
2020-03-20 | 21:04 | 49.955
2020-03-20 | 21:04 | 49.955
2020-03-20 | 21:04 | 49.951
2020-03-20 | 21:04 | 49.952
2020-03-20 | 21:04 | 49.951
2020-03-20 | 21:04 | 49.952
2020-03-20 | 21:04 | 49.95
2020-03-20 | 21:04 | 49.945
2020-03-20 | 21:04 | 49.942
2020-03-20 | 21:04 | 49.94
2020-03-20 | 21:04 | 49.938
2020-03-20 | 21:04 | 49.936
2020-03-20 | 21:04 | 49.934
2020-03-20 | 21:04 | 49.931
2020-03-20 | 21:04 | 49.929
2020-03-20 | 21:04 | 49.928
2020-03-20 | 21:04 | 49.927
2020-03-20 | 21:04 | 49.927
2020-03-20 | 21:04 | 49.927
2020-03-20 | 21:04 | 49.926
2020-03-20 | 21:04 | 49.924
2020-03-20 | 21:04 | 49.921
2020-03-20 | 21:04 | 49.919
2020-03-20 | 21:04 | 49.919
2020-03-20 | 21:04 | 49.92
2020-03-20 | 21:04 | 49.92
2020-03-20 | 21:04 | 49.921
2020-03-20 | 21:04 | 49.923
2020-03-20 | 21:04 | 49.924
2020-03-20 | 21:04 | 49.923
2020-03-20 | 21:04 | 49.923
2020-03-20 | 21:04 | 49.922
2020-03-20 | 21:04 | 49.923
2020-03-20 | 21:04 | 49.923
2020-03-20 | 21:04 | 49.921
2020-03-20 | 21:04 | 49.922
2020-03-20 | 21:04 | 49.922
2020-03-20 | 21:04 | 49.922
2020-03-20 | 21:04 | 49.921
2020-03-20 | 21:04 | 49.921
2020-03-20 | 21:05 | 49.921
2020-03-20 | 21:05 | 49.924
2020-03-20 | 21:05 | 49.925
2020-03-20 | 21:05 | 49.927
2020-03-20 | 21:05 | 49.93
2020-03-20 | 21:05 | 49.933
2020-03-20 | 21:05 | 49.934
2020-03-20 | 21:05 | 49.934
2020-03-20 | 21:05 | 49.934
2020-03-20 | 21:05 | 49.931
2020-03-20 | 21:05 | 49.93
2020-03-20 | 21:05 | 49.927
2020-03-20 | 21:05 | 49.924
2020-03-20 | 21:05 | 49.922
2020-03-20 | 21:05 | 49.922
2020-03-20 | 21:05 | 49.923
2020-03-20 | 21:05 | 49.923
2020-03-20 | 21:05 | 49.923
2020-03-20 | 21:05 | 49.923
2020-03-20 | 21:05 | 49.923
2020-03-20 | 21:05 | 49.923
2020-03-20 | 21:05 | 49.925
2020-03-20 | 21:05 | 49.927
2020-03-20 | 21:05 | 49.926
2020-03-20 | 21:05 | 49.928
2020-03-20 | 21:05 | 49.929
2020-03-20 | 21:05 | 49.929
2020-03-20 | 21:05 | 49.93
2020-03-20 | 21:05 | 49.932
2020-03-20 | 21:05 | 49.934
2020-03-20 | 21:05 | 49.938
2020-03-20 | 21:05 | 49.94
2020-03-20 | 21:05 | 49.939
2020-03-20 | 21:05 | 49.937
2020-03-20 | 21:05 | 49.935
2020-03-20 | 21:05 | 49.931
2020-03-20 | 21:05 | 49.928
2020-03-20 | 21:05 | 49.925
2020-03-20 | 21:05 | 49.919
2020-03-20 | 21:05 | 49.915
2020-03-20 | 21:05 | 49.913
2020-03-20 | 21:05 | 49.911
2020-03-20 | 21:05 | 49.91
2020-03-20 | 21:05 | 49.912
2020-03-20 | 21:05 | 49.915
2020-03-20 | 21:05 | 49.919
2020-03-20 | 21:05 | 49.922
2020-03-20 | 21:05 | 49.925
2020-03-20 | 21:05 | 49.927
2020-03-20 | 21:05 | 49.93
2020-03-20 | 21:05 | 49.933
2020-03-20 | 21:05 | 49.932
2020-03-20 | 21:05 | 49.934
2020-03-20 | 21:05 | 49.934
2020-03-20 | 21:05 | 49.935
2020-03-20 | 21:05 | 49.936
2020-03-20 | 21:05 | 49.936
2020-03-20 | 21:05 | 49.933
2020-03-20 | 21:05 | 49.933
2020-03-20 | 21:06 | 49.933
2020-03-20 | 21:06 | 49.933
2020-03-20 | 21:06 | 49.936
2020-03-20 | 21:06 | 49.938
2020-03-20 | 21:06 | 49.94
2020-03-20 | 21:06 | 49.941
2020-03-20 | 21:06 | 49.942
2020-03-20 | 21:06 | 49.944
2020-03-20 | 21:06 | 49.945
2020-03-20 | 21:06 | 49.945
2020-03-20 | 21:06 | 49.947
2020-03-20 | 21:06 | 49.949
2020-03-20 | 21:06 | 49.951
2020-03-20 | 21:06 | 49.952
2020-03-20 | 21:06 | 49.953
2020-03-20 | 21:06 | 49.953
2020-03-20 | 21:06 | 49.951
2020-03-20 | 21:06 | 49.951
2020-03-20 | 21:06 | 49.951
2020-03-20 | 21:06 | 49.951
2020-03-20 | 21:06 | 49.953
2020-03-20 | 21:06 | 49.953
2020-03-20 | 21:06 | 49.953
2020-03-20 | 21:06 | 49.953
2020-03-20 | 21:06 | 49.952
2020-03-20 | 21:06 | 49.955
2020-03-20 | 21:06 | 49.958
2020-03-20 | 21:06 | 49.96
2020-03-20 | 21:06 | 49.961
2020-03-20 | 21:06 | 49.961
2020-03-20 | 21:06 | 49.962
2020-03-20 | 21:06 | 49.964
2020-03-20 | 21:06 | 49.963
2020-03-20 | 21:06 | 49.964
2020-03-20 | 21:06 | 49.967
2020-03-20 | 21:06 | 49.968
2020-03-20 | 21:06 | 49.969
2020-03-20 | 21:06 | 49.971
2020-03-20 | 21:06 | 49.968
2020-03-20 | 21:06 | 49.968
2020-03-20 | 21:06 | 49.969
2020-03-20 | 21:06 | 49.967
2020-03-20 | 21:06 | 49.967
2020-03-20 | 21:06 | 49.966
2020-03-20 | 21:06 | 49.966
2020-03-20 | 21:06 | 49.966
2020-03-20 | 21:06 | 49.965
2020-03-20 | 21:06 | 49.967
2020-03-20 | 21:06 | 49.97
2020-03-20 | 21:06 | 49.972
2020-03-20 | 21:06 | 49.972
2020-03-20 | 21:06 | 49.969
2020-03-20 | 21:06 | 49.969
2020-03-20 | 21:06 | 49.968
2020-03-20 | 21:06 | 49.966
2020-03-20 | 21:06 | 49.965
2020-03-20 | 21:06 | 49.965
2020-03-20 | 21:06 | 49.968
2020-03-20 | 21:06 | 49.97
2020-03-20 | 21:06 | 49.973
2020-03-20 | 21:06 | 49.974
2020-03-20 | 21:07 | 49.974
2020-03-20 | 21:07 | 49.973
2020-03-20 | 21:07 | 49.974
2020-03-20 | 21:07 | 49.975
2020-03-20 | 21:07 | 49.973
2020-03-20 | 21:07 | 49.973
2020-03-20 | 21:07 | 49.973
2020-03-20 | 21:07 | 49.976
2020-03-20 | 21:07 | 49.98
2020-03-20 | 21:07 | 49.979
2020-03-20 | 21:07 | 49.98
2020-03-20 | 21:07 | 49.978
2020-03-20 | 21:07 | 49.979
2020-03-20 | 21:07 | 49.98
2020-03-20 | 21:07 | 49.982
2020-03-20 | 21:07 | 49.982
2020-03-20 | 21:07 | 49.982
2020-03-20 | 21:07 | 49.983
2020-03-20 | 21:07 | 49.986
2020-03-20 | 21:07 | 49.988
2020-03-20 | 21:07 | 49.991
2020-03-20 | 21:07 | 49.991
2020-03-20 | 21:07 | 49.993
2020-03-20 | 21:07 | 49.992
2020-03-20 | 21:07 | 49.996
2020-03-20 | 21:07 | 49.999
2020-03-20 | 21:07 | 50
2020-03-20 | 21:07 | 50.001
2020-03-20 | 21:07 | 50.003
2020-03-20 | 21:07 | 50.005
2020-03-20 | 21:07 | 50.006
2020-03-20 | 21:07 | 50.008
2020-03-20 | 21:07 | 50.008
2020-03-20 | 21:07 | 50.007
2020-03-20 | 21:07 | 50.003
2020-03-20 | 21:07 | 50.001
2020-03-20 | 21:07 | 49.999
2020-03-20 | 21:07 | 49.996
2020-03-20 | 21:07 | 49.995
2020-03-20 | 21:07 | 49.995
2020-03-20 | 21:07 | 49.993
2020-03-20 | 21:07 | 49.994
2020-03-20 | 21:07 | 49.995
2020-03-20 | 21:07 | 49.998
2020-03-20 | 21:07 | 50
2020-03-20 | 21:07 | 50
2020-03-20 | 21:07 | 50.005
2020-03-20 | 21:07 | 50.008
2020-03-20 | 21:07 | 50.011
2020-03-20 | 21:07 | 50.012
2020-03-20 | 21:07 | 50.012
2020-03-20 | 21:07 | 50.01
2020-03-20 | 21:07 | 50.013
2020-03-20 | 21:07 | 50.01
2020-03-20 | 21:07 | 50.015
2020-03-20 | 21:07 | 50.019
2020-03-20 | 21:07 | 50.021
2020-03-20 | 21:07 | 50.024
2020-03-20 | 21:07 | 50.026
2020-03-20 | 21:08 | 50.024
2020-03-20 | 21:08 | 50.022
2020-03-20 | 21:08 | 50.021
2020-03-20 | 21:08 | 50.02
2020-03-20 | 21:08 | 50.017
2020-03-20 | 21:08 | 50.014
2020-03-20 | 21:08 | 50.011
2020-03-20 | 21:08 | 50.008
2020-03-20 | 21:08 | 50.005
2020-03-20 | 21:08 | 50.002
2020-03-20 | 21:08 | 49.999
2020-03-20 | 21:08 | 49.998
2020-03-20 | 21:08 | 49.996
2020-03-20 | 21:08 | 49.996
2020-03-20 | 21:08 | 49.995
2020-03-20 | 21:08 | 49.997
2020-03-20 | 21:08 | 50
2020-03-20 | 21:08 | 50.002
2020-03-20 | 21:08 | 50
2020-03-20 | 21:08 | 50
2020-03-20 | 21:08 | 50
2020-03-20 | 21:08 | 50.004
2020-03-20 | 21:08 | 50.009
2020-03-20 | 21:08 | 50.012
2020-03-20 | 21:08 | 50.014
2020-03-20 | 21:08 | 50.013
2020-03-20 | 21:08 | 50.014
2020-03-20 | 21:08 | 50.016
2020-03-20 | 21:08 | 50.016
2020-03-20 | 21:08 | 50.016
2020-03-20 | 21:08 | 50.017
2020-03-20 | 21:08 | 50.018
2020-03-20 | 21:08 | 50.019
2020-03-20 | 21:08 | 50.02
2020-03-20 | 21:08 | 50.019
2020-03-20 | 21:08 | 50.02
2020-03-20 | 21:08 | 50.019
2020-03-20 | 21:08 | 50.016
2020-03-20 | 21:08 | 50.012
2020-03-20 | 21:08 | 50.01
2020-03-20 | 21:08 | 50.012
2020-03-20 | 21:08 | 50.013
2020-03-20 | 21:08 | 50.016
2020-03-20 | 21:08 | 50.015
2020-03-20 | 21:08 | 50.014
2020-03-20 | 21:08 | 50.016
2020-03-20 | 21:08 | 50.018
2020-03-20 | 21:08 | 50.016
2020-03-20 | 21:08 | 50.013
2020-03-20 | 21:08 | 50.012
2020-03-20 | 21:08 | 50.012
2020-03-20 | 21:08 | 50.01
2020-03-20 | 21:08 | 50.008
2020-03-20 | 21:08 | 50.009
2020-03-20 | 21:08 | 50.009
2020-03-20 | 21:08 | 50.01
2020-03-20 | 21:08 | 50.012
2020-03-20 | 21:08 | 50.015
2020-03-20 | 21:08 | 50.015
2020-03-20 | 21:08 | 50.015
2020-03-20 | 21:08 | 50.017
2020-03-20 | 21:09 | 50.018
2020-03-20 | 21:09 | 50.019
2020-03-20 | 21:09 | 50.018
2020-03-20 | 21:09 | 50.021
2020-03-20 | 21:09 | 50.026
2020-03-20 | 21:09 | 50.029
2020-03-20 | 21:09 | 50.031
2020-03-20 | 21:09 | 50.032
2020-03-20 | 21:09 | 50.031
2020-03-20 | 21:09 | 50.028
2020-03-20 | 21:09 | 50.027
2020-03-20 | 21:09 | 50.026
2020-03-20 | 21:09 | 50.025
2020-03-20 | 21:09 | 50.027
2020-03-20 | 21:09 | 50.028
2020-03-20 | 21:09 | 50.031
2020-03-20 | 21:09 | 50.032
2020-03-20 | 21:09 | 50.032
2020-03-20 | 21:09 | 50.035
2020-03-20 | 21:09 | 50.037
2020-03-20 | 21:09 | 50.038
2020-03-20 | 21:09 | 50.038
2020-03-20 | 21:09 | 50.038
2020-03-20 | 21:09 | 50.037
2020-03-20 | 21:09 | 50.036
2020-03-20 | 21:09 | 50.033
2020-03-20 | 21:09 | 50.034
2020-03-20 | 21:09 | 50.034
2020-03-20 | 21:09 | 50.033
2020-03-20 | 21:09 | 50.029
2020-03-20 | 21:09 | 50.026
2020-03-20 | 21:09 | 50.025
2020-03-20 | 21:09 | 50.023
2020-03-20 | 21:09 | 50.022
2020-03-20 | 21:09 | 50.02
2020-03-20 | 21:09 | 50.02
2020-03-20 | 21:09 | 50.017
2020-03-20 | 21:09 | 50.014
2020-03-20 | 21:09 | 50.012
2020-03-20 | 21:09 | 50.012
2020-03-20 | 21:09 | 50.011
2020-03-20 | 21:09 | 50.009
2020-03-20 | 21:09 | 50.008
2020-03-20 | 21:09 | 50.006
2020-03-20 | 21:09 | 50.007
2020-03-20 | 21:09 | 50.007
2020-03-20 | 21:09 | 50.001
2020-03-20 | 21:09 | 49.999
2020-03-20 | 21:09 | 49.999
2020-03-20 | 21:09 | 50
2020-03-20 | 21:09 | 50
2020-03-20 | 21:09 | 50.005
2020-03-20 | 21:09 | 50.01
2020-03-20 | 21:09 | 50.013
2020-03-20 | 21:09 | 50.016
2020-03-20 | 21:09 | 50.016
2020-03-20 | 21:09 | 50.018
2020-03-20 | 21:09 | 50.018
2020-03-20 | 21:09 | 50.017
2020-03-20 | 21:10 | 50.02
2020-03-20 | 21:10 | 50.018
2020-03-20 | 21:10 | 50.018
2020-03-20 | 21:10 | 50.02
2020-03-20 | 21:10 | 50.02
2020-03-20 | 21:10 | 50.02
2020-03-20 | 21:10 | 50.02
2020-03-20 | 21:10 | 50.021
2020-03-20 | 21:10 | 50.021
2020-03-20 | 21:10 | 50.022
2020-03-20 | 21:10 | 50.022
2020-03-20 | 21:10 | 50.024
2020-03-20 | 21:10 | 50.022
2020-03-20 | 21:10 | 50.024
2020-03-20 | 21:10 | 50.021
2020-03-20 | 21:10 | 50.017
2020-03-20 | 21:10 | 50.012
2020-03-20 | 21:10 | 50.009
2020-03-20 | 21:10 | 50.007
2020-03-20 | 21:10 | 50.005
2020-03-20 | 21:10 | 50.008
2020-03-20 | 21:10 | 50.011
2020-03-20 | 21:10 | 50.017
2020-03-20 | 21:10 | 50.019
2020-03-20 | 21:10 | 50.025
2020-03-20 | 21:10 | 50.026
2020-03-20 | 21:10 | 50.028
2020-03-20 | 21:10 | 50.031
2020-03-20 | 21:10 | 50.031
2020-03-20 | 21:10 | 50.032
2020-03-20 | 21:10 | 50.03
2020-03-20 | 21:10 | 50.027
2020-03-20 | 21:10 | 50.026
2020-03-20 | 21:10 | 50.027
2020-03-20 | 21:10 | 50.026
2020-03-20 | 21:10 | 50.026
2020-03-20 | 21:10 | 50.029
2020-03-20 | 21:10 | 50.032
2020-03-20 | 21:10 | 50.033
2020-03-20 | 21:10 | 50.036
2020-03-20 | 21:10 | 50.037
2020-03-20 | 21:10 | 50.037
2020-03-20 | 21:10 | 50.038
2020-03-20 | 21:10 | 50.041
2020-03-20 | 21:10 | 50.039
2020-03-20 | 21:10 | 50.039
2020-03-20 | 21:10 | 50.037
2020-03-20 | 21:10 | 50.035
2020-03-20 | 21:10 | 50.034
2020-03-20 | 21:10 | 50.032
2020-03-20 | 21:10 | 50.031
2020-03-20 | 21:10 | 50.032
2020-03-20 | 21:10 | 50.034
2020-03-20 | 21:10 | 50.034
2020-03-20 | 21:10 | 50.037
2020-03-20 | 21:10 | 50.04
2020-03-20 | 21:10 | 50.039
2020-03-20 | 21:10 | 50.039
2020-03-20 | 21:10 | 50.043
2020-03-20 | 21:10 | 50.042
2020-03-20 | 21:10 | 50.044
2020-03-20 | 21:11 | 50.048
2020-03-20 | 21:11 | 50.05
2020-03-20 | 21:11 | 50.051
2020-03-20 | 21:11 | 50.049
2020-03-20 | 21:11 | 50.051
2020-03-20 | 21:11 | 50.053
2020-03-20 | 21:11 | 50.054
2020-03-20 | 21:11 | 50.056
2020-03-20 | 21:11 | 50.058
2020-03-20 | 21:11 | 50.058
2020-03-20 | 21:11 | 50.054
2020-03-20 | 21:11 | 50.053
2020-03-20 | 21:11 | 50.051
2020-03-20 | 21:11 | 50.048
2020-03-20 | 21:11 | 50.05
2020-03-20 | 21:11 | 50.053
2020-03-20 | 21:11 | 50.056
2020-03-20 | 21:11 | 50.056
2020-03-20 | 21:11 | 50.059
2020-03-20 | 21:11 | 50.06
2020-03-20 | 21:11 | 50.062
2020-03-20 | 21:11 | 50.061
2020-03-20 | 21:11 | 50.061
2020-03-20 | 21:11 | 50.058
2020-03-20 | 21:11 | 50.055
2020-03-20 | 21:11 | 50.049
2020-03-20 | 21:11 | 50.041
2020-03-20 | 21:11 | 50.033
2020-03-20 | 21:11 | 50.022
2020-03-20 | 21:11 | 50.013
2020-03-20 | 21:11 | 50.006
2020-03-20 | 21:11 | 50
2020-03-20 | 21:11 | 49.996
2020-03-20 | 21:11 | 49.99
2020-03-20 | 21:11 | 49.989
2020-03-20 | 21:11 | 49.99
2020-03-20 | 21:11 | 49.99
2020-03-20 | 21:11 | 49.994
2020-03-20 | 21:11 | 49.995
2020-03-20 | 21:11 | 49.995
2020-03-20 | 21:11 | 49.994
2020-03-20 | 21:11 | 49.996
2020-03-20 | 21:11 | 49.997
2020-03-20 | 21:11 | 49.995
2020-03-20 | 21:11 | 49.997
2020-03-20 | 21:11 | 49.995
2020-03-20 | 21:11 | 49.994
2020-03-20 | 21:11 | 49.996
2020-03-20 | 21:11 | 49.997
2020-03-20 | 21:11 | 49.997
2020-03-20 | 21:11 | 49.998
2020-03-20 | 21:11 | 50
2020-03-20 | 21:11 | 50.001
2020-03-20 | 21:11 | 50.003
2020-03-20 | 21:11 | 50.005
2020-03-20 | 21:11 | 50.005
2020-03-20 | 21:11 | 50.009
2020-03-20 | 21:11 | 50.009
2020-03-20 | 21:11 | 50.007
2020-03-20 | 21:12 | 50.005
2020-03-20 | 21:12 | 50.004
2020-03-20 | 21:12 | 50.002
2020-03-20 | 21:12 | 50
2020-03-20 | 21:12 | 50.002
2020-03-20 | 21:12 | 50.003
2020-03-20 | 21:12 | 50.004
2020-03-20 | 21:12 | 50.007
2020-03-20 | 21:12 | 50.003
2020-03-20 | 21:12 | 50.002
2020-03-20 | 21:12 | 49.998
2020-03-20 | 21:12 | 49.995
2020-03-20 | 21:12 | 49.993
2020-03-20 | 21:12 | 49.994
2020-03-20 | 21:12 | 49.991
2020-03-20 | 21:12 | 49.989
2020-03-20 | 21:12 | 49.986
2020-03-20 | 21:12 | 49.983
2020-03-20 | 21:12 | 49.978
2020-03-20 | 21:12 | 49.978
2020-03-20 | 21:12 | 49.974
2020-03-20 | 21:12 | 49.972
2020-03-20 | 21:12 | 49.97
2020-03-20 | 21:12 | 49.968
2020-03-20 | 21:12 | 49.968
2020-03-20 | 21:12 | 49.97
2020-03-20 | 21:12 | 49.971
2020-03-20 | 21:12 | 49.969
2020-03-20 | 21:12 | 49.969
2020-03-20 | 21:12 | 49.965
2020-03-20 | 21:12 | 49.961
2020-03-20 | 21:12 | 49.957
2020-03-20 | 21:12 | 49.956
2020-03-20 | 21:12 | 49.955
2020-03-20 | 21:12 | 49.955
2020-03-20 | 21:12 | 49.955
2020-03-20 | 21:12 | 49.957
2020-03-20 | 21:12 | 49.956
2020-03-20 | 21:12 | 49.959
2020-03-20 | 21:12 | 49.96
2020-03-20 | 21:12 | 49.956
2020-03-20 | 21:12 | 49.955
2020-03-20 | 21:12 | 49.956
2020-03-20 | 21:12 | 49.957
2020-03-20 | 21:12 | 49.954
2020-03-20 | 21:12 | 49.956
2020-03-20 | 21:12 | 49.957
2020-03-20 | 21:12 | 49.959
2020-03-20 | 21:12 | 49.959
2020-03-20 | 21:12 | 49.958
2020-03-20 | 21:12 | 49.959
2020-03-20 | 21:12 | 49.958
2020-03-20 | 21:12 | 49.959
2020-03-20 | 21:12 | 49.962
2020-03-20 | 21:12 | 49.962
2020-03-20 | 21:12 | 49.961
2020-03-20 | 21:12 | 49.963
2020-03-20 | 21:12 | 49.963
2020-03-20 | 21:12 | 49.964
2020-03-20 | 21:12 | 49.963
2020-03-20 | 21:12 | 49.962
2020-03-20 | 21:13 | 49.965
2020-03-20 | 21:13 | 49.965
2020-03-20 | 21:13 | 49.966
2020-03-20 | 21:13 | 49.967
2020-03-20 | 21:13 | 49.967
2020-03-20 | 21:13 | 49.965
2020-03-20 | 21:13 | 49.966
2020-03-20 | 21:13 | 49.965
2020-03-20 | 21:13 | 49.963
2020-03-20 | 21:13 | 49.965
2020-03-20 | 21:13 | 49.968
2020-03-20 | 21:13 | 49.967
2020-03-20 | 21:13 | 49.97
2020-03-20 | 21:13 | 49.97
2020-03-20 | 21:13 | 49.968
2020-03-20 | 21:13 | 49.967
2020-03-20 | 21:13 | 49.966
2020-03-20 | 21:13 | 49.963
2020-03-20 | 21:13 | 49.963
2020-03-20 | 21:13 | 49.959
2020-03-20 | 21:13 | 49.957
2020-03-20 | 21:13 | 49.958
2020-03-20 | 21:13 | 49.954
2020-03-20 | 21:13 | 49.953
2020-03-20 | 21:13 | 49.953
2020-03-20 | 21:13 | 49.952
2020-03-20 | 21:13 | 49.956
2020-03-20 | 21:13 | 49.954
2020-03-20 | 21:13 | 49.956
2020-03-20 | 21:13 | 49.954
2020-03-20 | 21:13 | 49.952
2020-03-20 | 21:13 | 49.954
2020-03-20 | 21:13 | 49.954
2020-03-20 | 21:13 | 49.954
2020-03-20 | 21:13 | 49.955
2020-03-20 | 21:13 | 49.956
2020-03-20 | 21:13 | 49.955
2020-03-20 | 21:13 | 49.954
2020-03-20 | 21:13 | 49.952
2020-03-20 | 21:13 | 49.952
2020-03-20 | 21:13 | 49.952
2020-03-20 | 21:13 | 49.953
2020-03-20 | 21:13 | 49.956
2020-03-20 | 21:13 | 49.957
2020-03-20 | 21:13 | 49.957
2020-03-20 | 21:13 | 49.959
2020-03-20 | 21:13 | 49.959
2020-03-20 | 21:13 | 49.96
2020-03-20 | 21:13 | 49.961
2020-03-20 | 21:13 | 49.961
2020-03-20 | 21:13 | 49.959
2020-03-20 | 21:13 | 49.961
2020-03-20 | 21:13 | 49.961
2020-03-20 | 21:13 | 49.962
2020-03-20 | 21:13 | 49.962
2020-03-20 | 21:13 | 49.961
2020-03-20 | 21:13 | 49.963
2020-03-20 | 21:13 | 49.963
2020-03-20 | 21:13 | 49.963
2020-03-20 | 21:14 | 49.962
2020-03-20 | 21:14 | 49.963
2020-03-20 | 21:14 | 49.961
2020-03-20 | 21:14 | 49.958
2020-03-20 | 21:14 | 49.958
2020-03-20 | 21:14 | 49.957
2020-03-20 | 21:14 | 49.956
2020-03-20 | 21:14 | 49.956
2020-03-20 | 21:14 | 49.956
2020-03-20 | 21:14 | 49.954
2020-03-20 | 21:14 | 49.954
2020-03-20 | 21:14 | 49.954
2020-03-20 | 21:14 | 49.955
2020-03-20 | 21:14 | 49.954
2020-03-20 | 21:14 | 49.952
2020-03-20 | 21:14 | 49.949
2020-03-20 | 21:14 | 49.951
2020-03-20 | 21:14 | 49.951
2020-03-20 | 21:14 | 49.952
2020-03-20 | 21:14 | 49.952
2020-03-20 | 21:14 | 49.951
2020-03-20 | 21:14 | 49.95
2020-03-20 | 21:14 | 49.949
2020-03-20 | 21:14 | 49.948
2020-03-20 | 21:14 | 49.946
2020-03-20 | 21:14 | 49.945
2020-03-20 | 21:14 | 49.946
2020-03-20 | 21:14 | 49.95
2020-03-20 | 21:14 | 49.952
2020-03-20 | 21:14 | 49.956
2020-03-20 | 21:14 | 49.957
2020-03-20 | 21:14 | 49.961
2020-03-20 | 21:14 | 49.961
2020-03-20 | 21:14 | 49.962
2020-03-20 | 21:14 | 49.962
2020-03-20 | 21:14 | 49.965
2020-03-20 | 21:14 | 49.966
2020-03-20 | 21:14 | 49.964
2020-03-20 | 21:14 | 49.961
2020-03-20 | 21:14 | 49.958
2020-03-20 | 21:14 | 49.955
2020-03-20 | 21:14 | 49.952
2020-03-20 | 21:14 | 49.95
2020-03-20 | 21:14 | 49.944
2020-03-20 | 21:14 | 49.942
2020-03-20 | 21:14 | 49.942
2020-03-20 | 21:14 | 49.941
2020-03-20 | 21:14 | 49.94
2020-03-20 | 21:14 | 49.939
2020-03-20 | 21:14 | 49.941
2020-03-20 | 21:14 | 49.944
2020-03-20 | 21:14 | 49.946
2020-03-20 | 21:14 | 49.942
2020-03-20 | 21:14 | 49.942
2020-03-20 | 21:14 | 49.942
2020-03-20 | 21:14 | 49.936
2020-03-20 | 21:14 | 49.933
2020-03-20 | 21:14 | 49.931
2020-03-20 | 21:14 | 49.929
2020-03-20 | 21:14 | 49.929
2020-03-20 | 21:14 | 49.93
2020-03-20 | 21:15 | 49.931
2020-03-20 | 21:15 | 49.932
2020-03-20 | 21:15 | 49.934
2020-03-20 | 21:15 | 49.938
2020-03-20 | 21:15 | 49.942
2020-03-20 | 21:15 | 49.944
2020-03-20 | 21:15 | 49.945
2020-03-20 | 21:15 | 49.946
2020-03-20 | 21:15 | 49.948
2020-03-20 | 21:15 | 49.949
2020-03-20 | 21:15 | 49.95
2020-03-20 | 21:15 | 49.949
2020-03-20 | 21:15 | 49.95
2020-03-20 | 21:15 | 49.951
2020-03-20 | 21:15 | 49.954
2020-03-20 | 21:15 | 49.954
2020-03-20 | 21:15 | 49.953
2020-03-20 | 21:15 | 49.951
2020-03-20 | 21:15 | 49.952
2020-03-20 | 21:15 | 49.955
2020-03-20 | 21:15 | 49.955
2020-03-20 | 21:15 | 49.955
2020-03-20 | 21:15 | 49.957
2020-03-20 | 21:15 | 49.957
2020-03-20 | 21:15 | 49.958
2020-03-20 | 21:15 | 49.957
2020-03-20 | 21:15 | 49.958
2020-03-20 | 21:15 | 49.964
2020-03-20 | 21:15 | 49.971
2020-03-20 | 21:15 | 49.974
2020-03-20 | 21:15 | 49.977
2020-03-20 | 21:15 | 49.976
2020-03-20 | 21:15 | 49.973
2020-03-20 | 21:15 | 49.969
2020-03-20 | 21:15 | 49.966
2020-03-20 | 21:15 | 49.962
2020-03-20 | 21:15 | 49.958
2020-03-20 | 21:15 | 49.955
2020-03-20 | 21:15 | 49.95
2020-03-20 | 21:15 | 49.947
2020-03-20 | 21:15 | 49.95
2020-03-20 | 21:15 | 49.949
2020-03-20 | 21:15 | 49.95
2020-03-20 | 21:15 | 49.951
2020-03-20 | 21:15 | 49.952
2020-03-20 | 21:15 | 49.953
2020-03-20 | 21:15 | 49.957
2020-03-20 | 21:15 | 49.956
2020-03-20 | 21:15 | 49.956
2020-03-20 | 21:15 | 49.953
2020-03-20 | 21:15 | 49.955
2020-03-20 | 21:15 | 49.955
2020-03-20 | 21:15 | 49.956
2020-03-20 | 21:15 | 49.956
2020-03-20 | 21:15 | 49.957
2020-03-20 | 21:15 | 49.957
2020-03-20 | 21:15 | 49.958
2020-03-20 | 21:15 | 49.958
2020-03-20 | 21:15 | 49.959
2020-03-20 | 21:16 | 49.958
2020-03-20 | 21:16 | 49.958
2020-03-20 | 21:16 | 49.959
2020-03-20 | 21:16 | 49.958
2020-03-20 | 21:16 | 49.959
2020-03-20 | 21:16 | 49.959
2020-03-20 | 21:16 | 49.96
2020-03-20 | 21:16 | 49.959
2020-03-20 | 21:16 | 49.958
2020-03-20 | 21:16 | 49.958
2020-03-20 | 21:16 | 49.957
2020-03-20 | 21:16 | 49.956
2020-03-20 | 21:16 | 49.956
2020-03-20 | 21:16 | 49.959
2020-03-20 | 21:16 | 49.964
2020-03-20 | 21:16 | 49.968
2020-03-20 | 21:16 | 49.971
2020-03-20 | 21:16 | 49.974
2020-03-20 | 21:16 | 49.979
2020-03-20 | 21:16 | 49.986
2020-03-20 | 21:16 | 49.994
2020-03-20 | 21:16 | 50.001
2020-03-20 | 21:16 | 50.009
2020-03-20 | 21:16 | 50.015
2020-03-20 | 21:16 | 50.019
2020-03-20 | 21:16 | 50.025
2020-03-20 | 21:16 | 50.028
2020-03-20 | 21:16 | 50.029
2020-03-20 | 21:16 | 50.027
2020-03-20 | 21:16 | 50.027
2020-03-20 | 21:16 | 50.025
2020-03-20 | 21:16 | 50.024
2020-03-20 | 21:16 | 50.022
2020-03-20 | 21:16 | 50.02
2020-03-20 | 21:16 | 50.017
2020-03-20 | 21:16 | 50.017
2020-03-20 | 21:16 | 50.014
2020-03-20 | 21:16 | 50.012
2020-03-20 | 21:16 | 50.009
2020-03-20 | 21:16 | 50.011
2020-03-20 | 21:16 | 50.01
2020-03-20 | 21:16 | 50.009
2020-03-20 | 21:16 | 50.008
2020-03-20 | 21:16 | 50.009
2020-03-20 | 21:16 | 50.008
2020-03-20 | 21:16 | 50.005
2020-03-20 | 21:16 | 50.003
2020-03-20 | 21:16 | 50.003
2020-03-20 | 21:16 | 50
2020-03-20 | 21:16 | 49.998
2020-03-20 | 21:16 | 50.001
2020-03-20 | 21:16 | 50.002
2020-03-20 | 21:16 | 50.003
2020-03-20 | 21:16 | 50.006
2020-03-20 | 21:16 | 50.01
2020-03-20 | 21:16 | 50.011
2020-03-20 | 21:16 | 50.011
2020-03-20 | 21:16 | 50.013
2020-03-20 | 21:16 | 50.016
2020-03-20 | 21:16 | 50.016
2020-03-20 | 21:16 | 50.014
2020-03-20 | 21:17 | 50.014
2020-03-20 | 21:17 | 50.013
2020-03-20 | 21:17 | 50.009
2020-03-20 | 21:17 | 50.007
2020-03-20 | 21:17 | 50.003
2020-03-20 | 21:17 | 49.998
2020-03-20 | 21:17 | 49.995
2020-03-20 | 21:17 | 49.993
2020-03-20 | 21:17 | 49.992
2020-03-20 | 21:17 | 49.992
2020-03-20 | 21:17 | 49.993
2020-03-20 | 21:17 | 49.995
2020-03-20 | 21:17 | 49.992
2020-03-20 | 21:17 | 49.993
2020-03-20 | 21:17 | 49.996
2020-03-20 | 21:17 | 49.997
2020-03-20 | 21:17 | 49.999
2020-03-20 | 21:17 | 50.004
2020-03-20 | 21:17 | 50.006
2020-03-20 | 21:17 | 50.008
2020-03-20 | 21:17 | 50.012
2020-03-20 | 21:17 | 50.01
2020-03-20 | 21:17 | 50.008
2020-03-20 | 21:17 | 50.005
2020-03-20 | 21:17 | 50.001
2020-03-20 | 21:17 | 49.998
2020-03-20 | 21:17 | 49.996
2020-03-20 | 21:17 | 49.997
2020-03-20 | 21:17 | 50.002
2020-03-20 | 21:17 | 50.005
2020-03-20 | 21:17 | 50.006
2020-03-20 | 21:17 | 50.007
2020-03-20 | 21:17 | 50.008
2020-03-20 | 21:17 | 50.005
2020-03-20 | 21:17 | 50.001
2020-03-20 | 21:17 | 49.997
2020-03-20 | 21:17 | 49.992
2020-03-20 | 21:17 | 49.99
2020-03-20 | 21:17 | 49.989
2020-03-20 | 21:17 | 49.99
2020-03-20 | 21:17 | 49.992
2020-03-20 | 21:17 | 49.994
2020-03-20 | 21:17 | 49.996
2020-03-20 | 21:17 | 49.998
2020-03-20 | 21:17 | 50
2020-03-20 | 21:17 | 50.001
2020-03-20 | 21:17 | 50.004
2020-03-20 | 21:17 | 50.007
2020-03-20 | 21:17 | 50.013
2020-03-20 | 21:17 | 50.016
2020-03-20 | 21:17 | 50.017
2020-03-20 | 21:17 | 50.017
2020-03-20 | 21:17 | 50.016
2020-03-20 | 21:17 | 50.014
2020-03-20 | 21:17 | 50.012
2020-03-20 | 21:17 | 50.011
2020-03-20 | 21:17 | 50.011
2020-03-20 | 21:17 | 50.008
2020-03-20 | 21:17 | 50.004
2020-03-20 | 21:18 | 50.001
2020-03-20 | 21:18 | 49.998
2020-03-20 | 21:18 | 49.997
2020-03-20 | 21:18 | 49.994
2020-03-20 | 21:18 | 49.993
2020-03-20 | 21:18 | 49.993
2020-03-20 | 21:18 | 49.996
2020-03-20 | 21:18 | 49.995
2020-03-20 | 21:18 | 49.994
2020-03-20 | 21:18 | 49.997
2020-03-20 | 21:18 | 49.997
2020-03-20 | 21:18 | 49.999
2020-03-20 | 21:18 | 50.004
2020-03-20 | 21:18 | 50.009
2020-03-20 | 21:18 | 50.016
2020-03-20 | 21:18 | 50.019
2020-03-20 | 21:18 | 50.02
2020-03-20 | 21:18 | 50.02
2020-03-20 | 21:18 | 50.019
2020-03-20 | 21:18 | 50.022
2020-03-20 | 21:18 | 50.022
2020-03-20 | 21:18 | 50.019
2020-03-20 | 21:18 | 50.021
2020-03-20 | 21:18 | 50.02
2020-03-20 | 21:18 | 50.018
2020-03-20 | 21:18 | 50.017
2020-03-20 | 21:18 | 50.015
2020-03-20 | 21:18 | 50.013
2020-03-20 | 21:18 | 50.013
2020-03-20 | 21:18 | 50.013
2020-03-20 | 21:18 | 50.012
2020-03-20 | 21:18 | 50.01
2020-03-20 | 21:18 | 50.008
2020-03-20 | 21:18 | 50.007
2020-03-20 | 21:18 | 50.007
2020-03-20 | 21:18 | 50.01
2020-03-20 | 21:18 | 50.009
2020-03-20 | 21:18 | 50.011
2020-03-20 | 21:18 | 50.014
2020-03-20 | 21:18 | 50.013
2020-03-20 | 21:18 | 50.015
2020-03-20 | 21:18 | 50.017
2020-03-20 | 21:18 | 50.017
2020-03-20 | 21:18 | 50.017
2020-03-20 | 21:18 | 50.018
2020-03-20 | 21:18 | 50.016
2020-03-20 | 21:18 | 50.016
2020-03-20 | 21:18 | 50.017
2020-03-20 | 21:18 | 50.015
2020-03-20 | 21:18 | 50.012
2020-03-20 | 21:18 | 50.01
2020-03-20 | 21:18 | 50.008
2020-03-20 | 21:18 | 50.007
2020-03-20 | 21:18 | 50.008
2020-03-20 | 21:18 | 50.008
2020-03-20 | 21:18 | 50.009
2020-03-20 | 21:18 | 50.009
2020-03-20 | 21:18 | 50.005
2020-03-20 | 21:18 | 50.002
2020-03-20 | 21:18 | 49.999
2020-03-20 | 21:18 | 49.995
2020-03-20 | 21:19 | 49.991
2020-03-20 | 21:19 | 49.987
2020-03-20 | 21:19 | 49.985
2020-03-20 | 21:19 | 49.985
2020-03-20 | 21:19 | 49.987
2020-03-20 | 21:19 | 49.986
2020-03-20 | 21:19 | 49.99
2020-03-20 | 21:19 | 49.989
2020-03-20 | 21:19 | 49.987
2020-03-20 | 21:19 | 49.987
2020-03-20 | 21:19 | 49.991
2020-03-20 | 21:19 | 49.99
2020-03-20 | 21:19 | 49.986
2020-03-20 | 21:19 | 49.987
2020-03-20 | 21:19 | 49.985
2020-03-20 | 21:19 | 49.983
2020-03-20 | 21:19 | 49.982
2020-03-20 | 21:19 | 49.983
2020-03-20 | 21:19 | 49.982
2020-03-20 | 21:19 | 49.983
2020-03-20 | 21:19 | 49.983
2020-03-20 | 21:19 | 49.984
2020-03-20 | 21:19 | 49.984
2020-03-20 | 21:19 | 49.984
2020-03-20 | 21:19 | 49.982
2020-03-20 | 21:19 | 49.978
2020-03-20 | 21:19 | 49.976
2020-03-20 | 21:19 | 49.976
2020-03-20 | 21:19 | 49.971
2020-03-20 | 21:19 | 49.968
2020-03-20 | 21:19 | 49.969
2020-03-20 | 21:19 | 49.971
2020-03-20 | 21:19 | 49.971
2020-03-20 | 21:19 | 49.974
2020-03-20 | 21:19 | 49.977
2020-03-20 | 21:19 | 49.977
2020-03-20 | 21:19 | 49.976
2020-03-20 | 21:19 | 49.974
2020-03-20 | 21:19 | 49.973
2020-03-20 | 21:19 | 49.968
2020-03-20 | 21:19 | 49.965
2020-03-20 | 21:19 | 49.962
2020-03-20 | 21:19 | 49.959
2020-03-20 | 21:19 | 49.958
2020-03-20 | 21:19 | 49.955
2020-03-20 | 21:19 | 49.954
2020-03-20 | 21:19 | 49.952
2020-03-20 | 21:19 | 49.952
2020-03-20 | 21:19 | 49.953
2020-03-20 | 21:19 | 49.955
2020-03-20 | 21:19 | 49.957
2020-03-20 | 21:19 | 49.957
2020-03-20 | 21:19 | 49.961
2020-03-20 | 21:19 | 49.961
2020-03-20 | 21:19 | 49.959
2020-03-20 | 21:19 | 49.961
2020-03-20 | 21:19 | 49.959
2020-03-20 | 21:19 | 49.954
2020-03-20 | 21:19 | 49.953
2020-03-20 | 21:20 | 49.953
2020-03-20 | 21:20 | 49.95
2020-03-20 | 21:20 | 49.949
2020-03-20 | 21:20 | 49.948
2020-03-20 | 21:20 | 49.946
2020-03-20 | 21:20 | 49.945
2020-03-20 | 21:20 | 49.944
2020-03-20 | 21:20 | 49.946
2020-03-20 | 21:20 | 49.943
2020-03-20 | 21:20 | 49.939
2020-03-20 | 21:20 | 49.938
2020-03-20 | 21:20 | 49.936
2020-03-20 | 21:20 | 49.935
2020-03-20 | 21:20 | 49.932
2020-03-20 | 21:20 | 49.931
2020-03-20 | 21:20 | 49.932
2020-03-20 | 21:20 | 49.934
2020-03-20 | 21:20 | 49.938
2020-03-20 | 21:20 | 49.94
2020-03-20 | 21:20 | 49.943
2020-03-20 | 21:20 | 49.948
2020-03-20 | 21:20 | 49.952
2020-03-20 | 21:20 | 49.955
2020-03-20 | 21:20 | 49.954
2020-03-20 | 21:20 | 49.957
2020-03-20 | 21:20 | 49.956
2020-03-20 | 21:20 | 49.955
2020-03-20 | 21:20 | 49.956
2020-03-20 | 21:20 | 49.956
2020-03-20 | 21:20 | 49.957
2020-03-20 | 21:20 | 49.957
2020-03-20 | 21:20 | 49.955
2020-03-20 | 21:20 | 49.949
2020-03-20 | 21:20 | 49.945
2020-03-20 | 21:20 | 49.942
2020-03-20 | 21:20 | 49.939
2020-03-20 | 21:20 | 49.937
2020-03-20 | 21:20 | 49.932
2020-03-20 | 21:20 | 49.93
2020-03-20 | 21:20 | 49.931
2020-03-20 | 21:20 | 49.932
2020-03-20 | 21:20 | 49.935
2020-03-20 | 21:20 | 49.936
2020-03-20 | 21:20 | 49.938
2020-03-20 | 21:20 | 49.937
2020-03-20 | 21:20 | 49.937
2020-03-20 | 21:20 | 49.937
2020-03-20 | 21:20 | 49.935
2020-03-20 | 21:20 | 49.936
2020-03-20 | 21:20 | 49.938
2020-03-20 | 21:20 | 49.939
2020-03-20 | 21:20 | 49.94
2020-03-20 | 21:20 | 49.941
2020-03-20 | 21:20 | 49.942
2020-03-20 | 21:20 | 49.942
2020-03-20 | 21:20 | 49.941
2020-03-20 | 21:20 | 49.942
2020-03-20 | 21:20 | 49.94
2020-03-20 | 21:20 | 49.941
2020-03-20 | 21:20 | 49.939
2020-03-20 | 21:20 | 49.935
2020-03-20 | 21:21 | 49.932
2020-03-20 | 21:21 | 49.93
2020-03-20 | 21:21 | 49.93
2020-03-20 | 21:21 | 49.928
2020-03-20 | 21:21 | 49.927
2020-03-20 | 21:21 | 49.927
2020-03-20 | 21:21 | 49.926
2020-03-20 | 21:21 | 49.926
2020-03-20 | 21:21 | 49.927
2020-03-20 | 21:21 | 49.929
2020-03-20 | 21:21 | 49.928
2020-03-20 | 21:21 | 49.929
2020-03-20 | 21:21 | 49.931
2020-03-20 | 21:21 | 49.931
2020-03-20 | 21:21 | 49.935
2020-03-20 | 21:21 | 49.934
2020-03-20 | 21:21 | 49.935
2020-03-20 | 21:21 | 49.935
2020-03-20 | 21:21 | 49.937
2020-03-20 | 21:21 | 49.937
2020-03-20 | 21:21 | 49.937
2020-03-20 | 21:21 | 49.937
2020-03-20 | 21:21 | 49.939
2020-03-20 | 21:21 | 49.937
2020-03-20 | 21:21 | 49.935
2020-03-20 | 21:21 | 49.932
2020-03-20 | 21:21 | 49.93
2020-03-20 | 21:21 | 49.925
2020-03-20 | 21:21 | 49.923
2020-03-20 | 21:21 | 49.924
2020-03-20 | 21:21 | 49.922
2020-03-20 | 21:21 | 49.922
2020-03-20 | 21:21 | 49.924
2020-03-20 | 21:21 | 49.924
2020-03-20 | 21:21 | 49.926
2020-03-20 | 21:21 | 49.922
2020-03-20 | 21:21 | 49.922
2020-03-20 | 21:21 | 49.923
2020-03-20 | 21:21 | 49.921
2020-03-20 | 21:21 | 49.92
2020-03-20 | 21:21 | 49.922
2020-03-20 | 21:21 | 49.924
2020-03-20 | 21:21 | 49.923
2020-03-20 | 21:21 | 49.921
2020-03-20 | 21:21 | 49.921
2020-03-20 | 21:21 | 49.918
2020-03-20 | 21:21 | 49.918
2020-03-20 | 21:21 | 49.913
2020-03-20 | 21:21 | 49.912
2020-03-20 | 21:21 | 49.909
2020-03-20 | 21:21 | 49.905
2020-03-20 | 21:21 | 49.902
2020-03-20 | 21:21 | 49.898
2020-03-20 | 21:21 | 49.897
2020-03-20 | 21:21 | 49.899
2020-03-20 | 21:21 | 49.9
2020-03-20 | 21:21 | 49.902
2020-03-20 | 21:21 | 49.901
2020-03-20 | 21:21 | 49.903
2020-03-20 | 21:22 | 49.908
2020-03-20 | 21:22 | 49.911
2020-03-20 | 21:22 | 49.915
2020-03-20 | 21:22 | 49.92
2020-03-20 | 21:22 | 49.922
2020-03-20 | 21:22 | 49.926
2020-03-20 | 21:22 | 49.928
2020-03-20 | 21:22 | 49.929
2020-03-20 | 21:22 | 49.923
2020-03-20 | 21:22 | 49.915
2020-03-20 | 21:22 | 49.907
2020-03-20 | 21:22 | 49.897
2020-03-20 | 21:22 | 49.887
2020-03-20 | 21:22 | 49.881
2020-03-20 | 21:22 | 49.882
2020-03-20 | 21:22 | 49.883
2020-03-20 | 21:22 | 49.885
2020-03-20 | 21:22 | 49.882
2020-03-20 | 21:22 | 49.879
2020-03-20 | 21:22 | 49.88
2020-03-20 | 21:22 | 49.881
2020-03-20 | 21:22 | 49.884
2020-03-20 | 21:22 | 49.888
2020-03-20 | 21:22 | 49.889
2020-03-20 | 21:22 | 49.887
2020-03-20 | 21:22 | 49.885
2020-03-20 | 21:22 | 49.877
2020-03-20 | 21:22 | 49.873
2020-03-20 | 21:22 | 49.871
2020-03-20 | 21:22 | 49.868
2020-03-20 | 21:22 | 49.87
2020-03-20 | 21:22 | 49.872
2020-03-20 | 21:22 | 49.872
2020-03-20 | 21:22 | 49.869
2020-03-20 | 21:22 | 49.87
2020-03-20 | 21:22 | 49.872
2020-03-20 | 21:22 | 49.876
2020-03-20 | 21:22 | 49.882
2020-03-20 | 21:22 | 49.89
2020-03-20 | 21:22 | 49.896
2020-03-20 | 21:22 | 49.9
2020-03-20 | 21:22 | 49.904
2020-03-20 | 21:22 | 49.906
2020-03-20 | 21:22 | 49.908
2020-03-20 | 21:22 | 49.908
2020-03-20 | 21:22 | 49.908
2020-03-20 | 21:22 | 49.911
2020-03-20 | 21:22 | 49.914
2020-03-20 | 21:22 | 49.916
2020-03-20 | 21:22 | 49.919
2020-03-20 | 21:22 | 49.923
2020-03-20 | 21:22 | 49.926
2020-03-20 | 21:22 | 49.93
2020-03-20 | 21:22 | 49.933
2020-03-20 | 21:22 | 49.935
2020-03-20 | 21:22 | 49.933
2020-03-20 | 21:22 | 49.934
2020-03-20 | 21:22 | 49.933
2020-03-20 | 21:22 | 49.932
2020-03-20 | 21:22 | 49.934
2020-03-20 | 21:22 | 49.935
2020-03-20 | 21:23 | 49.938
2020-03-20 | 21:23 | 49.944
2020-03-20 | 21:23 | 49.946
2020-03-20 | 21:23 | 49.948
2020-03-20 | 21:23 | 49.946
2020-03-20 | 21:23 | 49.945
2020-03-20 | 21:23 | 49.943
2020-03-20 | 21:23 | 49.943
2020-03-20 | 21:23 | 49.942
2020-03-20 | 21:23 | 49.942
2020-03-20 | 21:23 | 49.941
2020-03-20 | 21:23 | 49.943
2020-03-20 | 21:23 | 49.944
2020-03-20 | 21:23 | 49.946
2020-03-20 | 21:23 | 49.949
2020-03-20 | 21:23 | 49.953
2020-03-20 | 21:23 | 49.954
2020-03-20 | 21:23 | 49.954
2020-03-20 | 21:23 | 49.957
2020-03-20 | 21:23 | 49.96
2020-03-20 | 21:23 | 49.961
2020-03-20 | 21:23 | 49.96
2020-03-20 | 21:23 | 49.96
2020-03-20 | 21:23 | 49.959
2020-03-20 | 21:23 | 49.959
2020-03-20 | 21:23 | 49.956
2020-03-20 | 21:23 | 49.952
2020-03-20 | 21:23 | 49.948
2020-03-20 | 21:23 | 49.947
2020-03-20 | 21:23 | 49.944
2020-03-20 | 21:23 | 49.941
2020-03-20 | 21:23 | 49.938
2020-03-20 | 21:23 | 49.936
2020-03-20 | 21:23 | 49.936
2020-03-20 | 21:23 | 49.934
2020-03-20 | 21:23 | 49.934
2020-03-20 | 21:23 | 49.935
2020-03-20 | 21:23 | 49.938
2020-03-20 | 21:23 | 49.941
2020-03-20 | 21:23 | 49.947
2020-03-20 | 21:23 | 49.951
2020-03-20 | 21:23 | 49.952
2020-03-20 | 21:23 | 49.955
2020-03-20 | 21:23 | 49.958
2020-03-20 | 21:23 | 49.956
2020-03-20 | 21:23 | 49.954
2020-03-20 | 21:23 | 49.954
2020-03-20 | 21:23 | 49.954
2020-03-20 | 21:23 | 49.955
2020-03-20 | 21:23 | 49.957
2020-03-20 | 21:23 | 49.961
2020-03-20 | 21:23 | 49.969
2020-03-20 | 21:23 | 49.976
2020-03-20 | 21:23 | 49.981
2020-03-20 | 21:23 | 49.983
2020-03-20 | 21:23 | 49.984
2020-03-20 | 21:23 | 49.986
2020-03-20 | 21:23 | 49.989
2020-03-20 | 21:23 | 49.988
2020-03-20 | 21:24 | 49.989
2020-03-20 | 21:24 | 49.99
2020-03-20 | 21:24 | 49.99
2020-03-20 | 21:24 | 49.99
2020-03-20 | 21:24 | 49.99
2020-03-20 | 21:24 | 49.99
2020-03-20 | 21:24 | 49.992
2020-03-20 | 21:24 | 49.994
2020-03-20 | 21:24 | 49.995
2020-03-20 | 21:24 | 49.999
2020-03-20 | 21:24 | 50.002
2020-03-20 | 21:24 | 50.007
2020-03-20 | 21:24 | 50.014
2020-03-20 | 21:24 | 50.016
2020-03-20 | 21:24 | 50.019
2020-03-20 | 21:24 | 50.018
2020-03-20 | 21:24 | 50.019
2020-03-20 | 21:24 | 50.019
2020-03-20 | 21:24 | 50.019
2020-03-20 | 21:24 | 50.018
2020-03-20 | 21:24 | 50.019
2020-03-20 | 21:24 | 50.02
2020-03-20 | 21:24 | 50.019
2020-03-20 | 21:24 | 50.02
2020-03-20 | 21:24 | 50.022
2020-03-20 | 21:24 | 50.024
2020-03-20 | 21:24 | 50.023
2020-03-20 | 21:24 | 50.025
2020-03-20 | 21:24 | 50.024
2020-03-20 | 21:24 | 50.021