## Service Requirements
Title | Routes to Market review for demand side flexibility Stage 1: industry engagement on barriers
Document | ESO Service Requirements V3
Date | 2024-05-21
|  |  | ESO Ancillary Services | [9 empty] | ESO Primary Balancing Market
Service Requirements | Requirement Description | Static FFR | Dynamic Containment | Dynamic Moderation | Dynamic Regulation | STOR | Fast Reserve | Quick Reserve | Slow Reserve | Balancing Reserve | Local Constraint Market | DFS | Balancing Mechanism
Required to be a Balancing and Settlement Code (BSC) Party | The rules and governance arrangements for electricity balancing and settlement in Great Britain. | NO | NO | NO | NO | NO | NO | NO | NO | YES | NO | NO | YES
Non-BM Party Accessible | Participate without being a Balancing Mechanism Party | Yes | YES (via ASDP) | YES (via ASDP) | YES (via ASDP) | YES | YES | YES (Not on Day 1) | YES | NO | YES | YES | NO
Operational Metering Required | A live feed to ESO control room to measure providers live service delivery | No | YES | YES | YES | YES | YES | YES | YES | YES | NO | NO | YES
Procurement Method | The type of mechanism used to procure the service | Pay as Clear (Capacity) | Pay as Clear (Capacity) | Pay as Clear (Capacity) | Pay as Clear (Capacity) | Pay as Clear (Capacity) | Pay as Bid (Utilisation) | Pay as Clear (Capacity) Pay as Bid (Utilisation) | Pay as Clear (Capacity) Pay as Bid (Utilisation) | Pay as Clear (Capacity) Pay as Bid (Utilisation) | Pay as Bid Day Ahead Auction [& Intra Day Auction] | Pay as bid tender | Pay as Bid Optional Market
Instruction Notice Period | Notice given to providers that they will need to respond to an instruction in the immediate future | N/A (automated dispatch) | N/A (automated dispatch) | N/A (automated dispatch) | N/A (automated dispatch) | 2 MINUTES | 5 MINUTES for Non BM | 0 MINUTE | Up to 2 MINUTES |  | 8 hrs (6 hrs) | 4+ hours | 2 MINUTES
Delivery Duration | Minimum amount of time that a provider must be able to provide its obligated delivery volume | 30 MINUTES | 15 MINUTES | 30 MINUTES | 60 MINUTES | 2 HOURS + | 15 MINUTES + | Up to 5 MINUTES (Min) | Up to 30 MINUTES (Min) | 1 MINUTE (MIN) 89 MINUTES (MAX) | 30 MINUTES (MIN) 24 HRS (MAX, NEEDS-DRIVEN) | 30 MINUTES + | 1 MINUTE +
Availability/utilisation period | the periods in which the service is made available or utilisation is committed (e.g., settlement periods, EFA block, committed blocks, etc.) | EFA Block | EFA Block | EFA Block | EFA Block | STOR windows |  | Settlement Period | 2 Hours | Settlement Period |  | settlement period
Asset Location Grouping Requirement | Requirement for where multiple assets within a unit must be located | National aggregation is permitted | GSP GROUP | GSP GROUP | GSP GROUP | GSP GROUP | GSP GROUP | GSP GROUP | GSP GROUP | GSP GROUP | PER INDIVIDUAL SCOTLAND GSP | NATIONAL | GSP GROUP
Asset metering permitted (vs boundary point metering system) | What type of metering is permitted? Some services only allow boundary meter data whilst others allow metering behind the boundary i.e. asset metering | The data is aggregated by the provider and therefore they can use asset level metering if they want to. | Asset metering permitted | Asset metering permitted | Asset metering permitted |  |  | Asset metering permitted | Asset metering permitted |  | Boundary metering only | Asset level metering permitted (but with ad hoc boundary meter checks)
Operational Meter Accuracy Required | The accuracy rating required of physical meters providing operational metering | No operational metering required. | +/-1% | +/-1% | +/-1% | +/-1% | +/-1% | +/-1% | +/-1% | +/-1% | N/a | +2.5% / -3.5% (COP11 DERIVED) | +/-1%
Operational Meter Refresh Frequency | The frequency that the physical meter captures real-time data snapshots | No operational metering required. | 1Hz | 1Hz | 1Hz | 1Hz | 1Hz | 1Hz | 1Hz | 1 Hz | n/a | N/A | 1Hz
Operational Metering Latency | Operational metering data must reach the ESO Control Room within this time | No operational metering required. | 5s | 5s | 5s | 5s | 5s | 5s | 5s | 5s | n/a | N/A | 5 SECONDS
Operational Metering Signal Type | The type of electrical data collected for operational metering | No operational metering required. | Active power and SoE | Active power and SoE | Active power and SoE | Active Power | Active Power | Active Power | Active Power | Active Power | n/a | N/A | ACTIVE POWER
Performance Meter Refresh Frequency | The frequency that the physical meter captures real-time data snapshots (e.g. 20Hz= 20 snapshots per second) | 1Hz performance data | 20Hz | 20Hz | 2Hz or 20Hz | Every 15 Seconds. Service Providers can submit duplicate meter reads for up to a minute |  | N/A - Phase 1 1Hz (TBC) - Phase 2 | 1Hz (TBC) | 1Hz | Half Hourly | Half Hourly | N/A
Aggregation /Virtual Lead Party (VLP) Route Available | The option of having more than a single asset within a unit | YES | YES | YES | YES | YES |  | YES | YES | YES | YES | YES | YES
Service Registration Platform | The platform used to register to enter the service | SINGLE MARKETS PLATFORM | SINGLE MARKETS PLATFORM | SINGLE MARKETS PLATFORM | SINGLE MARKETS PLATFORM | Salesforce | SINGLE MARKETS PLATFORM | SINGLE MARKETS PLATFORM | SINGLE MARKETS PLATFORM | SINGLE MARKETS PLATFORM | www.picloflex.com | SINGLE MARKETS PLATFORM | BM registration
Settlement Registration Platform | The platform to register and submit settlement data | via email | DAP | DAP | DAP |  |  | TBC | TBC | Automated from BM and Elexon systems | CALCULATE/REPORTING ON PICLOFLEX | RDT SharePoint solution | Elexon
Time to respond to instruction | Time to show unit ramping has began | up to 30 SECONDS | 0.5 SECONDS | 0.5 SECONDS | 2 SECONDS | 2 MINUTES | 2 MINUTES | 0 MINUTE | Up to 2 MINUTES | 2 MINUTES | 1hr | 4+ hours | 2-89mins
Max time to full delivery from Instruction | Time taken to reach procured volume delivery | up to 30 SECONDS | 1 SECOND | 1 SECOND | 10 SECONDS | 20 MINUTES | 2 MINUTES | 1 MINUTE | 15 MINUTES | 10 MINUTES | (n/a - SP dependent) | N/A | As per unit parameters
Ramping requirements | The specific requirements of the service in relation to ramping up or down of delivery | [6 empty] | No maximum ramping limits for ramping up or down from instruction | No ramping greater than 50% capacity per 30s period allowed |  |  | N/A | N/A
Procurement Platform | The platform that providers use to receive instructions and bid into the service | offline auction tool | EAC | EAC | EAC | SALESFORCE | VIA THE BM FOR BM PARTIES OR ASDP FOR ANCILLARY SERVICES FOR NON-BM PARTIES | EAC | EAC | EAC | www.picloflex.com | RDT solution | BM
Offers Availability Payments | Payments to providers in exchange for being ready to respond to instructions at any time | YES | YES | YES | YES | YES | YES | YES | YES | YES | NO | NO | NO
Minimum MW Delivery Required | The minimum MW delivery rate that a unit must exceed to enter the service | 1MW | 1MW | 1MW | 1MW | 3MW | 25MW | 1MW | 1MW | 1MW | NONE (1 kW) | 1MW | 1MW
Baselining | The historical baseline data used to calculate delivery performance and inform settlement | the second immediately before the frequency event is used as the baseline. | 60 minute nomination via PN or nBM equivalent | 60 minute nomination via PN or nBM equivalent | 60 minute nomination via PN or nBM equivalent | 60 minute nomination via PN or nBM equivalent | 60 minute nomination via PN or nBM equivalent | PN/ 60 MINUTE NOMINATION | PN/ 60 MINUTE NOMINATION | PN | FORECAST AT BID (+/-24 SPs) - PERFORMANCE IS CHECKED ON NON-ACCEPTANCE SPs/DAYS | P376 (BSC) (within-day adjustment element removed) | PN
Maximum Recovery Period | Minimum time between separate instructions and providers must be ready to respond again | N/A | N/A | N/A | N/A | 20 HOURS |  | 3 MINUTES | 30 MINUTES (TBC) | N/A | N/A | N/A | UNIT SELF DEFINE for recovery at 0MW only
Settlement or performance monitoring required? |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | SETTLEMENT AND PERFORMANCE (LCM is proposing to mirror DFS C16 conditional use of Asset metering) | All performance is reviewed by market monitoring team to ensure accurate payment vs delivered. | Yes (settlement of BOAs) and performance monitoring via imbalance
Generation/demand turn down service or demand turn up service? | Does the service require the provider to export or import power to the grid | Export or reduce demand | BOTH | BOTH | BOTH | Export | Export | BOTH | BOTH | BOTH |  | Demand Turn Down | BOTH
Unit volume cap | Maximum amount of MW volume per unit registered in the service | N/A | 100MW | 50MW | 50MW CAP | N/A | N/A | 300MW | N/A | N/A |  | 100MW CAP | N/A
Auction contract length | How long the providers delivery contract lasts | 4 hours | 4 hours | 4 hours | 4 hours | STOR Window | N/A | 30 minutes | 2 Hours | 30 minutes |  | 30 minutes | N/A
Instruction Trigger | What triggers a request to deliver the contracted volume | Frequency Deviation | Frequency Deviation | Frequency Deviation | Frequency Deviation | ENCC manual instruction | ENCC manual instruction | ENCC manual instruction | ENCC manual instruction | ENCC manual instruction |  | Tender result will be seen as instruction | ENCC manual instruction
Notes | [7 empty] | We have recently consulted on Quick Reserve and have yet to progress to EBR Article 18 consultation | We have yet to consult on Slow Reserve and the above requirements are to be confirmed |  |  | Derogation expired 1 May 24.

## Baselines Table
Service | 60 minute nomination via Physical Notification or non-BM equivalent | 60 minute nomination via Physical Notification | P376 (BSC) | Forecast at bid (+/-24 SPs) | Historic peak
Balancing Mechanism | Yes
Quick Reserve Phase 1 |  | Yes
Quick Reserve Phase 2 | Yes
Slow Reserve | Yes
Dynamic Containment | Yes
Dynamic Moderation | Yes
Dynamic Regulation | Yes
Local Constraints Market |  |  |  | Yes
Demand Flexibility Service |  |  | Yes (within-day adjustment removed)